|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Matthew Dempsey, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 20 May 2024 |
| Re: | 82 Camden High Street London NW1 0LT |
| Proposal: | Variation of condition 2 (approved plans) of ref: 2022/3459/P dated 14/10/2022, for; Minor Material Amendment (S73) to amend Condition 2 (Approved plans) of ref: 2021/3936/P dated 07/07/2022 for 'Retrospective application to change the use of the ground and basement unit from a mixed A1 (retail), A3 (cafe) and A4 (bar) Sui Generis use to Class E (b) and retention of air-conditioning unit on the rear at first floor level and a cooking extract grille at the rear.' |
| Reference: | Planning application ref. 2023/3646/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

Acoustic assessments has been submitted to support a planning application

for the change the use of the ground and basement unit from a mixed A1 (retail), A3 (cafe) and A4 (bar) Sui Generis use to Class E (b) and retention of air-conditioning unit on the rear at first floor level and a cooking extract grille at the rear of 82 Camden High Street London NW1 0LT

Appropriate noise guidelines have been followed within both the reports such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, BS 8233 Guidance on sound insulation and noise reduction for buildings, Camden Council’s Local Plan, version June 2017 and BS 4142:2014 “Methods for rating and assessing industrial and commercial sound”.

The applicant’s latest assessment Report No. 202321058M1058C/1/2, dated 19th May 2023 have considered the typical background noise levels as the basis of the design noise criteria and mitigation mearsures required to meet local authority requirements.

The plant noise criteria have been adequately predicted  taking into consideration distance losses, surface acoustic reflections and, where applicable, screening provided by the building.

I am satisfied that the submitted acoustic submission meets our local plan guidelines and would not have an adverse impact on the nearest sensitive receivers with specified mitigation measures being installed.

Therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following revised conditions should you be mindful to grant the application.

Suggested conditions: (as additional mitigation is required)

Prior to use of the development the noise mitigation and attenuation measures shall be installed to ensure that the external noise level emitted from plant, machinery/ equipment will be lower than either the existing background noise level by at least 10dBA, by 15dBA where the source is tonal, as assessed according to “Methods for rating and assessing industrial and commercial sound” at the nearest and/or most affected noise sensitive premises with all machinery operating together at maximum capacity and thereafter be permanently retained. A post installation noise assessment shall be carried out to confirm compliance with the noise criteria and additional steps to mitigate noise shall be taken, as necessary.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967 652382