|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Henry Yeung, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 23 August 2024 |
| Re: | Acland Burghley School 93 Burghley Road London NW5 1UJ |
| Proposal: | Erection of a single-storey extension to the southeast facade of the main assembly hall building to provide accessible WCs and buried earth duct associated with a new ventilation system. |
| Reference: | Planning application ref. 2024/0864/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

A noise assessment has been submitted by the applicant for proposed refurbishment of of Acland Burghley School, 93 Burghley Road.

It is proposed to locate the new plant equipment to the south side of the lecture hall. The Hall is to be refurbished with new reconfiguration internally for stage and seating arrangement, the control room will be changed into a bar and box office and new ventilation will be installed in the hall consisting of mechanical supply at low level and passive extract above the stage. New toilets are proposed within the existing structure and a new extension is proposed, to accommodate a glazed corridor overlooking the external amphitheatre.

It is currently proposed that this supply air handling unit be housed within a new concrete plenum formed abutting the existing foundations off the western wall of the building. Fresh air will be drawn in via earth duct which leads to what is expected to be a tower incorporating louvres some 2-3m to the north of the AHU.

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, BS 8233 Guidance on sound insulation and noise reduction for buildings, BS 4142:2014 “Methods for rating and assessing industrial and commercial sound” and the Camden Council’s Local Plan, version June 2017.

The plant noise criteria have been adequately predicted  taking into consideration distance losses, surface acoustic reflections and, where applicable, screening provided by the building.

The assessment indicates that the proposed installation along with suggested future mitigation measures should be capable of achieving the Camden’s environmental noise criteria at the nearest and potentially most affected noise sensitive receptors.

I am satisfied that the submitted acoustic submission meets our local plan guidelines with the specified noise mitigation and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

The external noise level emitted from plant, machinery or equipment at the development with specified noise mitigation hereby approved shall be lower than the typical existing background noise level by at least 10dBA, by 15dBA where the source is tonal, as assessed according to BS4142:2014 at the nearest and/or most affected noise sensitive premises, with machinery operating at maximum capacity and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967 652382