|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Adam Afford, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 22 January 2025 |
| Re: | 12 Queensmead St John's Wood Park London Camden NW8 6RE |
| Proposal: | Works to rear garden including installation of 2 Air Source Heat Pumps (ASHP) and 1 Air Conditioning Condenser within acoustic enclosure panels, extension of existing raised terrace and associated landscaping works |
| Reference: | Planning application ref. 2024/4697/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

An acoustic assessment has been carried out to support the planning application for the proposed two air source heat pumps and one condenser unit are proposed at the south-eastern end of the rear garden.

The proposed air source heat pumps consist of 2No Daikin Altherma 3 High Capacity Monobloc air source heat pumps, the proposed air conditioning condenser consists of 1No Daikin RXYSCQ6TV1.

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, BS 8233 Guidance on sound insulation and noise reduction for buildings, Camden Council’s Local Plan, version June 2017 and BS 4142:2014 “Methods for rating and assessing industrial and commercial sound”..

The external plant is proposed within a sunken plant area at the south-eastern end of the rear garden of the property, to maximise distance and screening from the nearest noise sensitive properties. In addition, the vertical surfaces of the sunken plant area around the units will be fitted with acoustically absorptive panels to reduce acoustic reflections.

The plant noise criteria have been adequately predicted  taking into consideration distance losses, surface acoustic reflections and, where applicable, screening provided by the building. It is recommended that an enclosure is installed around the plant.

The assessment indicates that the proposed mechanical plant installation should be capable of achieving the Camden’s environmental noise criteria at the nearest and potentially most affected noise sensitive receptors.

I am satisfied that the submitted acoustic submission and assocoiated technical details meets our local plan guidelines and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

The external noise level emitted from plant, machinery or equipment at the development with specified noise mitigation hereby approved shall be lower than the typical existing background noise level by at least 10dBA, by 15dBA where the source is tonal, as assessed according to BS4142:2014 at the nearest and/or most affected noise sensitive premises, with machinery operating at maximum capacity and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967 652382