## Sheet1
| WWL Response | Status
Issue 1: The figures have been provided and the SAP / BRUKL worksheets and summaries to verify the figures. There is a slight difference in the total Carbon Offset which is stated in the Energy Statement Table 5.1 to be £61,612 but our calcualtions (due to rounding) state a total carbon offset of £61,560 for both the resi and non-resi areas. The GLA Carbon Emission reporting spreadsheet has not been provided which would confirm the carbon offset calculations. Note: If the development is to be phased then carbon reductions for each building should be provided to enable phase sign off of s106 carbon reduction clauses. ACTION: Provision of the GLA spreadsheet to confirm the carbon reduction figures for each building and carbon offset figures. Carbon reductions and carbon offset to be secured through s106. | Updated Report and GLA Spreadsheet to be provided. Ref: JATRD-WWL-RP-CS-XX-98-0002 and 20241007_Part_l_2021_gla_carbon_emission_reporting_spreadsheet_v2.0_0 Item has to be included in the S106 clauses.
Issue 2: The development is within the Heat Network Priority Areas and therefore the proposed development should future proof for future connection. ACTION: Secure future proofing for connection to heat networks through s106 | Allowance for future connection are shown in our Planning and Stage 2 information. Item has to be included in the S106 clauses.
Issue 3: The Strategy states that the proposed heat pump may be electric or gas powered. It is not clear what the carbon implications of either system are and if the carbon reduction figures presented are for the electric system and the impact if gas were to be the chosen technology. ACTION: Further information required. | Clarification: All electric systems have been proposed. No Nat Gas connection to the buildings has been allowed.
Issue 4: Ground source heat pump has been ruled out for technical reasons but it is not clear what these are. Ground conditions should be assessed to determine if this technology is feasible. ACTION: Further information required | Feasibility of GSHP clarified in document: 20250121 - GSHP Feasibility Additional Information-P01. GSHP was discounted early in the design process given the site location, limited available space within the site for this technology to be applied.
Issue 5: Indicative areas for PV shown and 94 solar PV panels over 182m2 with 38.53kWp indicated in the energy strategy but no roof top layout of panels provided and Proposed Plan level R1 indicates some differences in areas and again different in the Green Roof Plan in the BNG assessment. PV should be maximised and combined with green / blue roofs where feasible. Details of maintenance access including potential man safe systems should be considered in the design. ACTION: Further details of design layout and maintenance access requested. Condition recommended | Further design development is required, the design proposals have allocated the maximum roof area available for PV, ensuring a 1-meter gap from the edge of the panels to the parapet wall for maintenance purposes. This approach should eliminate the need for any man safe equipment. The designated area exceeds the minimum compliance requirements outlined in the Energy and Sustainability strategy. The final panel layout will be refined as the design progresses during stage 3 and 4, considering the requirements of the green roofs (Bauder system proposed to combine the green roofs and PV).(Additional information: Stage 2 Drawing: JATRD-WWL-DR-CS-XX-11-0002, Green-Roof-Systems-Bauder-Brochure).
Issue 6: Be seen reporting should be secured through the S106.ACTION: secure Be Seen reporting through s106 | Item has to be included in the S106 clauses.
Issue 7: The areas with non openable windows are largely in the residential blocks and clear justification is required of acoustic and or security concerns and consideration of secure nighttime ventilation options should be made. Active cooling through air tempering or air conditioning is not expected in residential areas and all efforts should be made to minimise the need. In addition it should be made clear that air tempering is only provided to the units with clearly justified reasons for non openable windows. Further investigation is required to incorporate measures to reduce the overheating risk in DSY2 and DSY3 scenarios without the need for further active cooling. Cooling of commercial and communal areas should also be clearly justified. ACTION: Further information required. | The acoustician's assessment identified that the elevation windows could not be used for ventilation purposes overnight to meet the requirements of Part O: Ventilation. Extensive modelling during Stage 2 investigated the feasibility of several measures: Acoustically treated louvers: This measure was discounted as large units would be required to achieve compliance, making it impractical due to cost and aesthetics. External blinds/shutters: Discounted because they would block incoming air, reducing the effectiveness of the windows for ventilation. Enhanced MVHR units: Increased flow rates alone would not mitigate overheating in the rooms. (this measures has been incorporated in the proposals). Window opening restrictions for safety: All window openings for PBSA require a minimum 100mm restriction for safety, limiting the viability of natural ventilation by reducing the available free area for fresh air ingress. Acoustic restrictions: Noise from roads and adjacent businesses limited the use of windows as a mitigation measure for overheating. Reference: Docs 20240814-OverheatingComments-JR_P01 (early stage iterative simulation examples). The overheating measures included to satisfy the requirements under Part O were maximized given the site's constraints in terms of acoustic impact and safety. It is important to note that all occupied cluster/studio, bedroom, and kitchen living spaces include access to natural ventilation through openable windows and doors. It is anticipated that the results under DSY 2 and 3 would improve when testing the occupied spaces without the acoustic restrictions, showing a reduced risk of overheating. Cooling the non-domestic element of the PBSA has been reduced and measures to reduce direct solar gain have been incorporated in the proposals. But given the limitations on openable windows and varied occupancy patterns and numbers this solution was deemed the most cost effective method to maintain comfort within this areas. Low energy VRF system providing heating and cooling have been proposed.
Issue 8: 175m2 of green roof is proposed but this is not clear where it is. There is an area identified in the Drainage Strategy but this is a location of green roof which is also identified for solar PV on the ‘Proposal plan level R1’. Other areas are identified in the BNG Assessment. Green blue roofs and solar PV should be maximised where feasible (see Issue 5). No planting or substrate details are provided at this stage or mention of potential to combine with blue roof or solar. We would require a substrate depth of 150mm. Further details are required. ACTION: Further details and clarification required and Condition recommended. | Greengage has confirmed that the BNG includes 0.0594 hectares (ha) of moderate condition biodiverse green roof, as presented in the report 552772ohOct24FV01_BNGA. These measurements account for the green roofs proposed in the new landscape design (Ref: 24002_GA-P-200-B_Proposed Green Roof Plan). A Bauder PV Mounted system has been considered, as noted in issue 5, to combine the green roofs and PV. HDR provided a clarification note on the green roof in the Jamestown Rd - Technical Note 002, in response to LLFA comments on 21.01.25. The proposal and information above show that both green roofs and PV have been maximized to meet the requirements set out in the Energy Strategy and BNG calculations.
Issue 9: 16.1 of the Sustainability Strategy refers to site wide water design proposals being developed and a commitment to 105l per person per day residential requirement. ACTION: Secure through condition. | To be included within conditions.
Issue 10: A greywater system has been discounted (section 5.5) without a full feasibility assessment which is required in our local plan for high water uses such as student accommodation. ACTION: An feasibility assessment for greywater Harvesting should be provided which should consider the following: • the cost of the system; • cost savings for owner/occupier over a 10 year period; • projected grey water generation; • projected demand for use of grey water; • water savings as a result of the grey water system; and • payback for the system. | Please find additional information on the greywater system. This measures was reviewed during the early design process and discounted due Space Limitations: system requires significant space for storage tanks and filtration units, which is a challenge to accommodate in the proposed site. Using greywater would require additional pipework to run through the building which has proven difficult to coordinate in the proposed buildings as space for accommodation has been given priority. Maintenance Requirements: Regular maintenance is essential to ensure the systems operate efficiently and safely. In urban areas, access for maintenance can be difficult and costly. Water Quality Concerns: Greywater contains contaminants that require thorough treatment before reuse. The benefits of these systems are reduced given the urban location of the proposed development, additionally given the location and site footprint. Considering the factors above, alternative water-saving measures have been recommended as a more practical and cost-effective solution to achieve low water demand in the proposed development. : Ref: 20250124 - Water Recycling Technical Note P01
Issue 11: The requirement of 60% for energy credits has not been met. The potential credits are available which would result in 65% which would achieve the standard. Therefore the potential credits should be targeted. ACTION: Target credits and secure through s106. | Updated Pre-assessment report targets 60% of the Energy Credits. Document updated and included in this response: Jamestown Road PBSA - BREEAM NC 2018 Tracker for planning - 20.01.25