## VENT SUM
14 Bedford Row - Ventilation Calculations
Non-Guestroom Ventilation
| ROOM | ROOM REF. | NO. OF PEOPLE | AREA | SUPPLY VENTILATION (L/s) |  | SUPPLY RUNNING TOTAL | SUPPLY RUNNING TOTAL | EXTRACT VENTILATION (L/s) |  | EXTRACT RUNNING TOTAL | EXTRACT RUNNING TOTAL
[5 empty] | MIN | MAX | MIN | MAX | MIN | MAX | MIN | MAX
BASEMENT | GUEST AMENITY | B32 | 6 |  | 60 | 60 |  |  | 54 | 54
| CORRIDOR | B30 |  | 15.1 | 9.06 | 9.06 | 69.06 | 69.06 |  |  | 54 | 54
| HR | B34 |  |  | 20 | 30 | 89.06 | 99.06 | 21 | 31 | 75 | 85
| CORRIDOR | B30 |  | 15.1 |  |  | 89.06 | 99.06 | 4.53 | 4.53 | 79.53 | 89.53
| STAFF BREAKOUT | B33 | 2 |  | 20 | 20 | 109.06 | 119.06 | 18 | 18 | 97.53 | 107.53
| DDA WC | B39 |  |  |  |  | 109.06 | 119.06 | 8 | 8 | 105.53 | 115.53
GROUND FLOOR | PLANT | G32 |  | 15.9 | 9.54 | 9.54 |  |  | 4.77 | 4.77
| CORRIDOR | G27 |  | 5.1 | 3.06 | 3.06 | 12.6 | 12.6 |  |  | 4.77 | 4.77
| HR | G29 |  |  | 20 | 30 | 32.6 | 42.6 | 21 | 31 | 25.77 | 35.77
| CORRIDOR | G27 |  | 5.1 |  |  | 32.6 | 42.6 | 1.53 | 1.53 | 27.3 | 37.3
[7 empty] | 141.66 | 161.66 |  |  | 132.83 | 152.83
FIRST FLOOR | HR | 123 |  |  | 30 | 45 |  |  | 21 | 46
| CORRIDOR | 119 |  | 8.7 | 5.22 | 5.22 |  | 50.22 |  |  |  | 46
| HR | 120 |  |  | 20 | 30 |  | 80.22 | 21 | 31 |  | 77
| CORRIDOR | 119 |  | 8.7 |  |  |  | 80.22 | 2.61 | 2.61 |  | 79.61
| HR | 122 |  |  | 30 | 45 |  | 125.22 | 21 | 46 |  | 125.61
| HR | 121 |  |  | 20 | 30 |  | 155.22 | 21 | 31 |  | 156.61
[8 empty] | 316.88 |  |  |  | 309.44
SECOND FLOOR | HR | 224 |  |  | 30 | 45 |  |  | 21 | 46
| CORRIDOR | 220 |  | 8.7 | 5.22 | 5.22 |  | 50.22 |  |  |  | 46
| HR | 221 |  |  | 20 | 30 |  | 80.22 | 21 | 31 |  | 77
| CORRIDOR | 220 |  | 8.7 |  |  |  | 80.22 | 2.61 | 2.61 |  | 79.61
| HR | 223 |  |  | 30 | 45 |  | 125.22 | 21 | 46 |  | 125.61
| HR | 222 |  |  | 20 | 30 |  | 155.22 | 21 | 31 |  | 156.61
[8 empty] | 472.1 |  |  |  | 466.05
THIRD FLOOR | HR | 324 |  |  | 30 | 45 |  |  | 21 | 46
| CORRIDOR | 321 |  | 8.8 | 5.28 | 5.28 |  | 50.28 |  |  |  | 46
| HR | 322 |  |  | 20 | 30 |  | 80.28 | 21 | 31 |  | 77
| CORRIDOR | 321 |  | 8.8 |  |  |  | 80.28 | 2.64 | 2.64 |  | 79.64
| HR | 323 |  |  | 30 | 45 |  | 125.28 | 21 | 46 |  | 125.64
[8 empty] | 597.38 |  |  |  | 591.69
FIRST FLOOR | HR | 131 |  |  | 20 | 20 |  |  | 21 | 21
| HR | 130 |  |  | 20 | 30 |  | 50 | 21 | 31 |  | 52
| CORRIDOR | 124 |  | 22.1 | 13.26 | 13.26 |  | 63.26 |  |  |  | 52
| HR | 129 |  |  | 20 | 30 |  | 93.26 | 21 | 31 |  | 83
| CORRIDOR | 124 |  | 22.1 |  |  |  |  | 6.63 | 6.63
| HR | 126 |  |  | 20 | 20 |  | 20 | 21 | 21 |  | 27.63
| HR | 127 |  |  | 20 | 30 |  | 50 | 21 | 31 |  | 58.63
| HR | 128 |  |  | 20 | 30 |  | 80 | 21 | 31 |  | 89.63
| HR | 125 |  |  | 20 | 20 |  | 100 | 21 | 21 |  | 110.63
[8 empty] | 193.26 |  |  |  | 193.63
SECOND FLOOR | HR | 233 |  |  | 20 | 20 |  |  | 21 | 21
| HR | 232 |  |  | 20 | 30 |  | 50 | 21 | 31 |  | 52
| HR | 231 |  |  | 20 | 30 |  | 80 | 21 | 31 |  | 83
| CORRIDOR | 226 |  | 22.1 | 13.26 | 13.26 |  | 93.26 |  |  |  | 83
| CORRIDOR | 226 |  | 22.1 |  |  |  |  | 6.63 | 6.63
| HR | 228 |  |  | 20 | 30 |  | 30 | 21 | 31 |  | 37.63
| HR | 229 |  |  | 20 | 30 |  | 60 | 21 | 31 |  | 68.63
| HR | 230 |  |  | 20 | 30 |  | 90 | 21 | 31 |  | 99.63
| HR | 227 |  |  | 20 | 30 |  | 120 | 21 | 31 |  | 130.63
[8 empty] | 213.26 |  |  |  | 213.63
[8 empty] | 406.52 |  |  |  | 407.26
THIRD FLOOR | HR | 329 |  |  | 20 | 20 |  |  | 21 | 21
| HR | 328 |  |  | 30 | 45 |  | 65 | 21 | 46 |  | 67
| CORRIDOR | 320 |  | 20.3 | 12.18 | 12.18 |  | 77.18 |  |  |  | 67
| CORRIDOR | 320 |  | 20.3 |  |  |  |  | 6.09 | 6.09
| HR | 326 |  |  | 20 | 30 |  | 30 | 21 | 31 |  | 37.09
| HR | 327 |  |  | 30 | 45 |  | 75 | 21 | 46 |  | 83.09
| HR | 325 |  |  | 20 | 30 |  | 105 | 21 | 31 |  | 114.09
[8 empty] | 182.18 |  |  |  | 181.09
[8 empty] | 588.7 |  |  |  | 588.35
[8 empty] | 1186.08 |  |  |  | 1180.04
FOURTH FLOOR | HR | 414 |  |  | 20 | 20 |  |  | 21 | 21
| HR | 415 |  |  | 20 | 30 |  | 50 | 21 | 31 |  | 52
| CORRIDOR | **** |  | 14.2 |  |  |  | 50 | 4.26 | 4.26 |  | 56.26
| CORRIDOR | **** |  | 14.2 | 8.52 | 8.52
| HR | 416 |  |  | 20 | 20 |  | 28.52 | 21 | 21 |  | 21
| HR | 417 |  |  | 20 | 30 |  | 58.52 | 21 | 31 |  | 52
[8 empty] | 108.52 |  |  |  | 108.26
THIRD FLOOR | HR | 314 |  |  | 20 | 30 |  |  | 21 | 31
| CORRIDOR | 313 |  | 12 |  |  |  | 30 | 3.6 | 3.6 |  | 34.6
| HR | 315 |  |  | 20 | 30 |  | 60 | 21 | 31 |  | 65.6
| HR | 318 |  |  | 20 | 30 |  |  | 21 | 31
| HR | 319 |  |  | 30 | 45 |  | 75 | 21 | 46 |  | 77
| HR | 316 |  |  | 20 | 30 |  | 105 | 21 | 31 |  | 108
| CORRIDOR | 313 |  | 12 | 7.2 | 7.2 |  | 112.2 |  |  |  | 108
[8 empty] | 172.2 |  |  |  | 173.6
[8 empty] | 280.72 |  |  |  | 281.86
SECOND FLOOR | HR | 214 |  |  | 20 | 30 |  |  | 21 | 31
| CORRIDOR | 213 |  | 12.6 |  |  |  | 30 | 3.78 | 3.78 |  | 34.78
| HR | 215 |  |  | 20 | 30 |  | 60 | 21 | 31 |  | 65.78
| HR | 217 |  |  | 30 | 45 |  |  | 21 | 46
| HR | 218 |  |  | 30 | 45 |  | 90 | 21 | 46 |  | 92
| HR | 216 |  |  | 20 | 30 |  | 120 | 21 | 31 |  | 123
| CORRIDOR | 213 |  | 12.6 | 7.56 | 7.56 |  | 127.56 |  |  |  | 123
[8 empty] | 187.56 |  |  |  | 188.78
[8 empty] | 468.28 |  |  |  | 470.64
FIRST FLOOR | HR | 114 |  |  | 20 | 30 |  |  | 21 | 31
| CORRIDOR | 113 |  | 21.7 |  |  |  | 30 | 6.51 | 6.51 |  | 37.51
| HR | 115 |  |  | 20 | 30 |  | 60 | 21 | 31 |  | 68.51
| CORRIDOR | 113 |  | 21.7 | 13.02 | 13.02
| HR | 117 |  |  | 20 | 30 |  | 43.02 | 21 | 31 |  | 31
| HR | 118 |  |  | 30 | 45 |  | 88.02 | 21 | 46 |  | 77
| HR | 116 |  |  | 20 | 30 |  | 118.02 | 21 | 31 |  | 108
[8 empty] | 178.02 |  |  |  | 176.51
[8 empty] | 646.3 |  |  |  | 647.15
BASEMENT | HR | B21 |  |  | 20 | 30 |  |  | 21 | 31
| HR | B14 |  |  | 20 | 30 |  | 60 | 21 | 31 |  | 62
| CORRIDOR | B17 |  | 17.3 |  |  |  | 60 | 5.19 | 5.19 |  | 67.19
| HR | B20 |  |  | 20 | 30 |  | 90 | 21 | 31 |  | 98.19
| STAFF B | B33 | 2 |  | 20 | 20 | 20 | 110 | 18 | 18 | 18 | 116.19
| HR | B19 |  |  | 20 | 30 |  | 140 | 21 | 31 |  | 147.19
| CORRIDOR | B17 |  | 17.3 | 10.38 | 10.38 |  | 150.38 |  |  |  | 147.19
GROUND FLOOR | DDA WC | G19 |  |  |  |  | 0 | 150.38 | 8 | 8 | 8 | 155.19
| HR | G15 |  |  | 30 | 45 |  | 691.3 | 21 | 46 |  | 693.15
| CORRIDOR | G14 |  | 5.8 |  |  |  | 691.3 | 1.74 | 1.74 |  | 694.89
| LOB/AMEN | G13 | 4 |  | 40 | 40 | 40 | 731.3 | 36 | 36 | 36 | 730.89
| CORRIDOR | G16 |  | 5.8 | 3.48 | 3.48 |  | 734.78 |  |  |  | 730.89
| CORRIDOR | G17 |  | 25.8 |  |  |  | 734.78 | 7.74 | 7.74 |  | 738.63
| HR | G18 |  |  | 30 | 45 |  | 779.78 | 21 | 46 |  | 784.63
[8 empty] | 930.16 |  |  |  | 939.82
BASEMENT | HR | B23 |  |  | 20 | 20 |  |  | 21 | 21
| CORRIDOR | B22 |  | 21.7 |  |  |  | 20 | 6.51 | 6.51 |  | 27.51
GROUND FLOOR | HR | G21 |  |  | 20 | 20 |  | 40 | 21 | 21 |  | 48.51
[8 empty] | 970.16 |  |  |  | 988.33
BASEMENT | HR | B25 |  |  | 20 | 20 |  |  | 21 | 21
GROUND | HR | G22 |  |  | 20 | 20 |  | 40 | 21 | 21 |  | 42
[8 empty] | 1010.16 |  |  |  | 1030.33
GROUND FLOOR | CORRIDOR | G20 |  | 25.8 | 15.48 | 15.48 |  | 1025.64 |  |  |  | 1030.33
| CORRIDOR | G23 |  | 8.9 |  |  |  | 1025.64 | 2.67 | 2.67 |  | 1033
BASEMENT | HR | B26 |  |  | 20 | 20 |  |  | 21 | 21
GROUND | HR | G24 |  |  | 20 | 20 |  | 40 | 21 | 21 |  | 42
[8 empty] | 1065.64 |  |  |  | 1075
BASEMENT | HR | B27 |  |  | 20 | 20 |  |  | 21 | 21
| CORRIDOR | B24 |  | 21.7 | 13.02 | 13.02 |  | 33.02 |  |  |  | 21
GROUND FLOOR | HR | G25 |  |  | 20 | 30 |  | 63.02 | 21 | 31 |  | 52
| CORRIDOR | G23 |  | 8.9 | 5.34 | 5.34 |  | 68.36 |  |  |  | 52
[8 empty] | 1134 |  |  |  | 1127
|  | AREA | VOLUME | m3/h | m3/s | l/s
| Bin Store | 27.1 | 67.75 | 677.5 | 0.18819 | 188.1944
| Bike Store | 34 | 85 | 85 | 0.023611 | 23.6111

## HR VENT LOADS
14 Bedford Row - Ventilation Calculations
Guestroom Ventilation
HOTEL ROOM | UNIT SUPPLY |  | BATHROOM EXTRACT |  | KITCHEN EXTRACT |  | TOTAL EXTRACT |  | ROOM CONNECTIONS
| MIN | MAX | MIN | MAX | MIN | MAX | MIN | MAX | SUPPLY | EXTRACT
114 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
115 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
116 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
117 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
118 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
120 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
121 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
122 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
123 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
125 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
126 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
127 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
128 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
129 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
130 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
131 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
214 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
215 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
216 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
217 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
218 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
221 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
222 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
223 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
224 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
227 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
228 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
229 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
230 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
231 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
232 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
233 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
314 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
315 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
316 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
318 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
319 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
322 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
323 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
324 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
325 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
326 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
327 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
328 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
329 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
414 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
415 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
416 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
417 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
B14 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
B19 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
B20 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
B21 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
B23 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
B25 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
B26 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
B27 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
B34 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
G15 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
G18 | 30 | 45 | 8 | 18 | 13 | 28 | 21 | 46 | 150x100 | 150x100
G21 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
G22 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
G24 | 20 | 20 | 8 | 8 | 13 | 13 | 21 | 21 | 150x100 | 150x100
G25 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
G29 | 20 | 30 | 8 | 12 | 13 | 19 | 21 | 31 | 150x100 | 150x100
CORRIDORS | SEE INDIVIDUAL CORRIDOR VENT RATES IN SCHEMATIC | [7 empty] | Ø100 | Ø100