## Sheet1
Existing |  |  |  | Proposed
Door Type | Description | Photo | Quantity | Works Required | Quantity | Door References | Additional Comments
A | Single leaf timber door with decorative panelling (4 panel door). Light grey painted finish. | #VALUE! | 5 | Replacement Recommended (as per schedule) | 2 | 0001:28 0006:28 | A like for like replacment is to be recommended to match the existing panelling. If a replacment is not permitted the works will be limited to the repairs as per the schedule.
|  |  |  | Repairs (as per schedule) | 3 | 0002:28 0003:28 0011:28 | 0011:28 No access at the time of the survey
B | Single leaf, timber 6 panel door. Two panels are glazed vision panels. Light grey painted finish. | #VALUE! | 1 | No fire rated on existing door set , recommended to replace all door set with a timber fd30 door set inclusive of following: 3x grade 13 hinges 15mm intumescent brush strips 1x overhead closer 2x FDKS fixed signage Full lock and latch 2x vp ( 170x510mm ) Digi lock | 1 | 0004:28 | A like for like replacment is to be recommended to match the existing panelling. If a replacment is not permitted the works will be limited to the repairs as per the schedule.
C | Single leaf timber 4 panel door with glazing present (vision panels). Light grey painted finish. | #VALUE! | 4 | Repairs (as per schedule) | 4 | 0005:28 0007:28 0008:28 0009:28
D | Single leaf, timber panelled door with vision panel. Surrounding glazing present (side light). Dark mahogony finish. | #VALUE! | 3 | Replacement Recommended (as per schedule) | 1 | 0013:28 | A like for like replacment is to be recommended to match the existing panelling. If a replacment is not permitted the works will be limited to the repairs as per the schedule.
|  |  |  | Repairs (as per schedule) | 2 | 0012:28 0020:28
E | Single leaf, timber panelled door. 1 nr panel replaced retrospectively with glazing. Dark mahogony finish. | #VALUE! | 1 | Due to excessive damage on door leaf all door set need to be replaced inclusive of following: 3x grade 13 hinges 2x FDKS fixed signage 1x overhead closer 15mm intumescent brush strips Full lock and latch including handles Thumb turn euro cylinder 1x vp ( 250x510mm ) | 1 | 0019:28 | A like for like replacment is to be recommended to match the existing panelling. If a replacment is not permitted the works will be limited to the repairs as per the schedule.
F | Double leaf, solid timber panelled door. | #VALUE! | 2 | No Access | 1 | 0030:28 | 0030:28: No access at the time of the survey, works will be limited to those recommended for door 0031:28.
|  |  |  | Due to listed doorset in situ, remedial works limited to: Surface mount brush strips(10mm ) 6 grade 13 hinges FDKS Sticker signage Leaf repair Frame repair | 1 | 0031:28 | 0031:28: *Due to extensive damage to door frame and leaf ,FD30 double door set replacement recommended inclusive of following: 6grade 13 hinges 10mm intumescent brush strips 4x AFDCK fixed signage 2x automatic door closers Full lock and latch 4x FDKS sticker signage
G | Single leaf, timber panelled door with decorative lead glazing. Surrounding glazing present. (Lead glazing arched fan light and adjacent windows). | #VALUE! | 1 | Due to listed doorset in situ, remedial works limited to: Surface mount brush strips(15mm ) 4 grade 13 hinges FDKS Sticker signage BE lipping, BE gap 23mm Face mounted drop down seal ( leaf 940mm) | 1 | 0032:28 | 0032:28 is believed to be an original door and is therefore considered of heritage significance. Works are limited to remedial works only to avoid loss of historic fabric.
H | Single leaf, timber panelled door. | #VALUE! | 1 | Due to listed doorset in situ, remedial works limited to: Surface mount brush strips(15mm ) 3 grade 13 hinges FDKS Sticker signage Face mounted drop down seal (leaf 680mm) Closer adjustment | 1 | 0033:28 | 0033:28 is believed to be an original door and is therefore considered of heritage significance. Works are limited to remedial works only to avoid loss of historic fabric.
I | Single leaf, timber panelled door. White painted finish. | #VALUE! | 1 | No Access | 1 | 0015:28 | 0015:28 is not believed to be original to the building and is therefore unlikely to be of heritage significance, however it has been included in this application to have confirmation that remedial works of a similar nature to those described will be permissible.
Total |  |  | 19 |  | 19