## Sheet1
Project - Kings Cross Methodist Church
Basement Impact Assessment - Action Query Tracker Responses |  |  | Rev P03 | Date: 24/04/25
Query No. | Subject | Query | Status | Response
1 | BIA | Justifications should be provided where a “No” response has been recorded | Open- see section 4.23 | GEA Response: Added justifications to Section 3.0
2 | Land Stability | Clarifications about the presence of trees on site are requested. | Open- see section 4.9 | GEA Response: Amended in report Section 3.0
3 | Land Stability | An outline sequence of construction, including detailed sketches of the proposed temporary and permanent works are requested. The depth of the proposed excavation and ground levels has been used inconsistently across the GMA/BIA. | Open- see section 4.12 and 4.13 | P&M Response: Refer to CS-01 to CS-03 for outline construction sequence sketches, which add to the listed sequenced outlined in the GEA BIA report Section 8.2 Page 20 GEA Resonse: Levels altered to match P&M levels and be consistent throughout report and GMA
4 | Land Stability | Geotechnical parameters used inconsistently. Unloading pressures estimated inconsistently across the BIA/GMA. | Open- see section 4.14 | GEA Response: Unloading amended in GMA and report to be consistent throughout
5 | BIA | Utility plans and confirmation of consultation with relevant asset owners are requested. | Open- see section 4.16 | P&M Response: Utility plans now included in the updated BIA. As stated in Section 10.3 of the BIA the expected ground movement as a result of the works is less than 2mm in magnitude, which is considered not to have a significant impact on the existing services below Crestfield Street.
6 | Land Stability | GMA should consider the excavation beneath the north lightwell and demonstrate how the boundary walls are to be retained. | Open- see section 4.18 | P&M Response: Existing north boundary wall foundations are understood to be formed at low-level, approximately +14.51m to +14.58m OD. Refer to trial pit investigations TP2 & TP6. Some sequenced underpinning (approx 600mm deep) is proposed along the boundary to approximately +14.00m OD. Much of the raised levels in the lightwell are suspected to be fill given the foundation levels found. Refer to Construction Sequence Sketch CS-03 for more info.
7 | Land Stability | Anticipated depth of geological units used inconsistently across the BIA/GMA. Clarifications regarding the stiffness parameters adopted for the Lambeth Group are requested. | Open- see section 4.19 and 4.20 | GEA Response: Unit levels and stiffness parameters amended in GMA and report to be consistent throughout
8 | Land Stability | Clarifications regarding the loadings used in PDisp are requested. Structural load drawings are requested for review. | Open-see section 4.21 | P&M Response: Please refer to Sketch GMA-099 Rev 2 showing loads where they are changing and used in the PDisp analysis. No vertical loads will be added to the boundary walls as the new structure will be built in board.
9 | Land Stability | PDisp Input and output data for short term movements are requested. | Open-see section 4.22 | GEA Response: Added to appendix
10 | Land Stability | Overall (total) ground movements calculated after offsetting heave movements. | Open- see section 4.23 | GEA Response: Added to appendix
11 | Land Stability | Clarifications regarding the loading on the contiguous piled wall section Pdisp. | Open- see section 4.24 | GEA Response: Added to Section 9.2 of report
12 | Land Stability | Clarification regarding re-entrant corners are requested. Surface levels are used inconsistently within XDisp and PDisp. Outline calculations for the adopted pile lengths are requested. Corner stiffening has been adopted for the installation curves to be reviewed. | Open-see section 4.26 to 4.30 | GEA response: Note about reentrant corners in previous report issue have been removed as it is not relevant in this case. Corner stiffening has been removed from all installations. A pile toe depth of 4 m below the formation level has been adopted as the pile wall will be fully propped.
13 | Land Stability | Clarifications regarding the sensitivity analysis are requested. The damage category for the neighbouring structures should be updated following revisions to the GMA. | Open- see section 4.31 and 4.32 | GEA Response: Sensitivity analysis updated and no elevated damage category determined for any adjacent structures.
14 | CPG | Compliance with requirements of the CPG | Open - Section 5.10 | P&M Query: It is assumed CPG requirements will be met if the above queries are closed. Please confirm.