|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Connie Marinetto, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 15 May 2025 |
| Re: | Royal Free Hospital Pond Street London Camden NW3 2QG |
| Proposal: | Replacement of existing Power Transformer System on upper third floor with new Power Transformer System and enclosure on lower third floor roof; and associated works |
| Reference: | Planning application ref. 2025/1237/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

An acoustic assessment has been carried out to support the planning application for the proposed new items of plant at the Royal Free Hospital (RFH), London.

The transformer is proposed to be located on the roof of the Medical School, approximately 6 m from the roof edge and approximately 24 m from the nearest noise-sensitive receptors. the transformer will be housed in an enclosure made of 18mm plywood encased in GRP

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, BS 8233 Guidance on sound insulation and noise reduction for buildings, Camden Council’s Local Plan, version June 2017 and BS 4142:2014 “Methods for rating and assessing industrial and commercial sound”.

The plant noise criteria have been adequately predicted  taking into consideration distance losses, surface acoustic reflections and, where applicable, screening provided by the building.

The assessment indicates that the proposed plant installation should be capable of achieving the Camden’s environmental noise criteria at the nearest and potentially most affected noise sensitive receptors.

I am satisfied that the submitted acoustic and assocoiated technical details meets our local plan guidelines and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

The external noise levels emitted from plant/ machinery/ equipment shall ensure that the rating level of the noise emitted from the proposed installation located at the site shall not exceed the existing background level at any noise sensitive premises when measured and corrected in accordance with BS4142:2014 +A1:2019 “Methods for rating and assessing industrial and commercial sound.”

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967 652382