NANDO’S CHICKENLAND LTD

UNIT 8, ONE SOUTHAMPTON ROW

LONDON WC1

NOISE ASSESSMENT

AUGUST 2009

NANDO’S CHICKENLAND LTD

UNIT 8, ONE SOUTHAMPTON ROW

LONDON WC1

NOISE ASSESSMENT

AUGUST 2009

JUNE 2002

The preparation of this report by KC Environmental Limited has been undertaken within the terms of the proposal using all reasonable skill and care.  KC Environmental Limited accepts no responsibility for the data provided by other bodies and no legal liability arising from the use by other persons of data or opinions contained in this report

| Project: 1076 | August 2009 |
| --- | --- |
| Prepared By: | Ken Collins |

KC environmental ltd

2 St John’s Place

Hove

BN3 2FJ

UK

Tel: +44 (0)1273 778945

Fax: +44 (0) 1273 778945

www.kcenvironmental.co.uk

CONTENTS

1.	Introduction	1

2.	Noise Units and Standards	2

3.	Noise Measurements	4

4	Noise Assessment	5

5	Conclusions	6

References

APPENDIX A - Results of Noise Survey

APPENDIX B – Calculated Noise Levels

# Introduction

  - Nando’s Chickenland Ltd (Nando’s) is proposing to operate a restaurant at Unit 8, One Southampton Row, London WC1. When granting planning permission for the restaurant, the London Borough of Camden (Camden) attached a condition relating to noise levels from fixed plant associated with the restaurant.

  - Condition 4 of Planning Permission 2009/1057/P states:

- “Noise levels at a point 1 metre external to sensitive facades shall be at least 5 dB(A) less than the existing background measurement (LA90), expressed in dB(A) when all plant/equipment are in operation unless the plant/equipment hereby permitted will have a noise that has a distinguishable, discrete continuous note (whine, hiss, screech, hum) and/or if there are distinct impulses (bangs, clicks, clatters, thumps), then the noise levels from that piece of plant/equipment at any sensitive facade shall be at least 10 dB(A) below the LA90, expressed in dB(A).

- Reason: To safeguard the amenities of the adjoining premises and the area generally in accordance with the requirements of policies SD6, SD7B, SD8 and Appendix 1 of the London Borough of Camden Replacement Unitary Development Plan.”

  - Nando’s has commissioned KC Environmental Limited (KCEL) to undertake a noise assessment of the proposed new plant.

  - As part of the assessment, a site visit and ambient noise monitoring has been undertaken, and the noise level due to the proposed plant has been calculated.  This report presents the results of the assessment.

# Noise Units and Standards

Noise Units

- 2.1	Noise is defined as unwanted sound.  The range of audible sound is from 0 dB to 140 dB.  The frequency response of the ear is usually taken to be about 18 Hz (number of oscillations per second) to 18000 Hz.  The ear does not respond equally to different frequencies at the same level.  It is more sensitive in the mid-frequency range than the lower and higher frequencies and because of this, the low and high frequency components of a sound are reduced in importance by applying a weighting (filtering) circuit to the noise measuring instrument.  The weighting which is most widely used and which correlates best with subjective response to noise is the dB(A) weighting.  This is an internationally accepted standard for noise measurements.

- 2.2	The "loudness" of a noise is a subjective parameter, but it is generally accepted that an increase/decrease of 10 dB(A) corresponds to a doubling/halving in perceived loudness.

- 2.3	External noise levels are rarely steady, but rise and fall according to activities within an area.  In an attempt to produce a figure that relates this variable noise level to subjective response, a number of noise indices have been developed.  These include:

i)	The LAmax noise level

This is the maximum noise level recorded over the measurement period.

ii)	The LAeq noise level

This is the "equivalent continuous A-weighted sound pressure level, in decibels", and is defined in British Standard BS 7445 [1] as the "value of the A-weighted sound pressure level of a continuous, steady sound that, within a specified time interval, T, has the same mean square sound pressure as a sound under consideration whose level varies with time".

It is a unit commonly used to describe construction noise and noise from industrial premises and is the most suitable unit for the description of other forms of environmental noise.  In more straightforward terms, it is a measure of energy within the varying noise.

iii)	The LA10 noise level

This is the noise level that is exceeded for 10% of the measurement period and gives an indication of the noisier levels.  It is a unit that has been used over many years for the measurement and assessment of road traffic noise.

iv)	The LA90 noise level

This is the noise level that is exceeded for 90% of the measurement period and gives an indication of the noise level during quieter periods.  It is often referred to as the background noise level and is used in the assessment of disturbance from industrial noise.

London Borough of Camden

- 2.4	WCC’s Condition 4 of Planning Permission 2009/1057/P states:

- “Noise levels at a point 1 metre external to sensitive facades shall be at least 5 dB(A) less than the existing background measurement (LA90), expressed in dB(A) when all plant/equipment are in operation unless the plant/equipment hereby permitted will have a noise that has a distinguishable, discrete continuous note (whine, hiss, screech, hum) and/or if there are distinct impulses (bangs, clicks, clatters, thumps), then the noise levels from that piece of plant/equipment at any sensitive facade shall be at least 10 dB(A) below the LA90, expressed in dB(A).

- Reason: To safeguard the amenities of the adjoining premises and the area generally in accordance with the requirements of policies SD6, SD7B, SD8 and Appendix 1 of the London Borough of Camden Replacement Unitary Development Plan.”

# Noise Measurements

- 3.1	Unattended noise monitoring was undertaken between 15:29 hours on Thursday 13 August 2009and 08:44 am on Friday 14 August 2009.

- 3.2	Measurements were undertaken on the roof of the building at a height of 1.5 metres, 1 metre outside the barrier enclosing the plant area, and thus represented the requirements specified in the Condition. Measurement periods of fifteen minutes were recorded for the duration of the survey.

3.3	The instrumentation used consisted of a Cirrus 822B sound level meter and Cirrus 511E acoustic calibrator. The sound level meter was calibrated both prior to and immediately following the surveys. No significant drift was noted.

3.4	During the survey, the meteorological conditions were suitable for noise measurements.

3.5	The full results of the survey are given in Appendix A of this report, but the average and lowest levels in the hour after the latest permitted closing time and in the hour before the earliest permitted opening time is given in Table 1 below.

Table 1: Summary of Results of Noise Measurements

|  | Average LA90 | Minimum LA90 | LAeq |
| --- | --- | --- | --- |
| Hour after closing time (00:00-01:00) | 49.1 | 48.3 | 51.3 |
| Hour before opening time (07:00-08:00) | 52.5 | 51.5 | 56.5 |

3.6	It is considered that 48 dB(A) is representative of the lowest LA90 noise level that would occur when the plant is permitted to operate, and has been used for that purpose in the assessment.

# Noise Assessment

- 4.1	The site is located on the north-west corner of Southampton Place and High Holborn, London WC1. Southampton Place and High Holborn are heavily trafficked, and there are significant numbers of pedestrians.

  - During the site visit, plant noise from other buildings was just audible at the measurement location, and was visible on other buildings. However, the dominant noise source was considered to be that caused by road traffic.

  - In general, it can be seen from the results of the noise survey that noise levels are relatively steady, with a few increases due to specific events.

  - The proposed plant is a single RHF kitchen extract fan and three condenser units, which will be positioned on the roof, within the absorbent barrier surrounding the plant area. Plant data has been obtained from measurements of similar plant at a number of other Nando’s sites, and this has been used in the calculations.

  - For the purposes of the assessment, it has been assumed that the plant would operate over the permitted hours.

  - The nearest noise sensitive location has been taken to be the nearest window to the proposed plant location, i.e. the top floor of 8 Southampton Place. However, this window is significantly lower than the roof of the development site, and is shielded from plant on the roof by the absorbent barrier surrounding the plant area on the roof, and the parapet of the building.

  - Based on the plan showing the location of the proposed plant and the associated screening, and the plant specification, it has been calculated that the noise level from the proposed plant would be 47 dB(A) at the façade of the top floor of 8 Southampton Place. This is only 1 dB below the lowest measured LA90 background noise level of 48 dB(A) during the period that the plant would be operating, and would therefore not meet the requirement specified in  Condition 4 of the Planning Permission.

  - With a standard acoustic enclosure, and a single attenuator fitted on the air-side of the RHF fan, as fitted at many other Nando’s restaurants, it has been calculated that the noise level from the proposed plant would be 23 dB(A) at the façade of the top floor of 8 Southampton Place. This is significantly more than 10 dB below the measured LA90 background noise level of 48 dB(A) during the period that the plant would be operating, and would thus easily meet the requirement specified in Condition 4 of the Planning Permission.

# Conclusions

- 5.1	Nando’s Chickenland Ltd is proposing to operate a restaurant at Unit 8, One Southampton Row, London WC1. When granting planning permission for the restaurant, the London Borough of Camden attached a condition relating to noise levels from fixed plant associated with the restaurant.

  - A noise assessment of the plant has been undertaken, including a site visit and ambient noise monitoring, and the noise level due to the proposed plant has been calculated.

  - In order to meet the requirements of the Planning Permission, a standard acoustic enclosure and a single attenuator fitted on the air-side of the RHF fan will be necessary, as fitted at many other Nando’s restaurants.

  - Based on the plan showing the location of the proposed plant, the associated screening, the plant specification and the proposed attenuation measures, it has been calculated that the noise level from the proposed plant would be 23 dB(A) at the façade of the top floor of 8 Southampton Place. This is significantly more than 10 dB below the lowest measured LA90 background noise level of 48 dB(A) during the period that the plant would be operating, and would thus easily meet the requirement specified in Condition 4 of the Planning Permission.

REFERENCES

  - British Standards Institution.  British Standard 7445: Description and Measurement of Environmental Noise, Part 1.  Guide to Quantities and Procedures, 1991.

APPENDIX A

Results of Noise Survey

| Date | Time | LAeq | LAmax | LA10 | LA90 |
| --- | --- | --- | --- | --- | --- |
| 13-Aug-09 | 15:29 | 58.2 | 76.1 | 58.7 | 53.7 |
| 13-Aug-09 | 15:44 | 61.9 | 81.8 | 59.0 | 53.7 |
| 13-Aug-09 | 15:59 | 56.5 | 66.8 | 58.6 | 54.1 |
| 13-Aug-09 | 16:14 | 56.9 | 75.4 | 58.5 | 53.8 |
| 13-Aug-09 | 16:29 | 57.0 | 73.7 | 58.3 | 53.3 |
| 13-Aug-09 | 16:44 | 55.2 | 64.9 | 56.7 | 53.4 |
| 13-Aug-09 | 16:59 | 58.0 | 74.8 | 58.6 | 53.6 |
| 13-Aug-09 | 17:14 | 57.0 | 73.4 | 58.8 | 53.4 |
| 13-Aug-09 | 17:29 | 54.9 | 63.4 | 56.5 | 53.3 |
| 13-Aug-09 | 17:44 | 58.0 | 79.9 | 56.4 | 53.2 |
| 13-Aug-09 | 17:59 | 54.8 | 61.7 | 56.2 | 53.1 |
| 13-Aug-09 | 18:14 | 55.9 | 70.0 | 57.3 | 53.7 |
| 13-Aug-09 | 18:29 | 56.1 | 69.7 | 57.9 | 53.3 |
| 13-Aug-09 | 18:44 | 57.7 | 80.0 | 57.6 | 53.4 |
| 13-Aug-09 | 18:59 | 56.0 | 67.1 | 58.5 | 53.2 |
| 13-Aug-09 | 19:14 | 57.4 | 74.4 | 59.9 | 53.1 |
| 13-Aug-09 | 19:29 | 54.2 | 62.0 | 55.4 | 52.9 |
| 13-Aug-09 | 19:44 | 53.3 | 59.2 | 54.4 | 52.1 |
| 13-Aug-09 | 19:59 | 53.5 | 62.6 | 55.4 | 51.2 |
| 13-Aug-09 | 20:14 | 53.0 | 67.7 | 53.7 | 50.9 |
| 13-Aug-09 | 20:29 | 54.3 | 68.9 | 55.7 | 50.7 |
| 13-Aug-09 | 20:44 | 51.9 | 58.7 | 54.5 | 49.9 |
| 13-Aug-09 | 20:59 | 53.8 | 70.1 | 53.8 | 49.4 |
| 13-Aug-09 | 21:14 | 52.2 | 66.5 | 53.5 | 49.4 |
| 13-Aug-09 | 21:29 | 52.0 | 65.4 | 53.6 | 49.6 |
| 13-Aug-09 | 21:44 | 51.3 | 61.6 | 52.6 | 49.7 |
| 13-Aug-09 | 21:59 | 53.9 | 62.4 | 55.9 | 50.1 |
| 13-Aug-09 | 22:14 | 55.4 | 70.3 | 56.5 | 50.3 |
| 13-Aug-09 | 22:29 | 59.4 | 81.8 | 53.6 | 48.9 |
| 13-Aug-09 | 22:44 | 54.2 | 71.4 | 54.5 | 49.4 |
| 13-Aug-09 | 22:59 | 51.4 | 62.7 | 52.6 | 50.0 |
| 13-Aug-09 | 23:14 | 53.4 | 63.4 | 55.7 | 50.3 |
| 13-Aug-09 | 23:29 | 51.7 | 61.8 | 54.0 | 49.7 |
| 13-Aug-09 | 23:44 | 50.9 | 59.0 | 52.3 | 49.5 |
| 13-Aug-09 | 23:59 | 51.4 | 59.5 | 53.2 | 49.6 |
| 14-Aug-09 | 0:14 | 51.0 | 59.7 | 52.5 | 49.4 |
| 14-Aug-09 | 0:29 | 51.0 | 58.1 | 53.2 | 48.9 |
| 14-Aug-09 | 0:44 | 51.6 | 67.3 | 53.1 | 48.3 |
| 14-Aug-09 | 0:59 | 55.3 | 68.2 | 58.7 | 48.8 |
| 14-Aug-09 | 1:14 | 49.3 | 57.0 | 50.5 | 48.1 |
| 14-Aug-09 | 1:29 | 48.9 | 55.0 | 50.0 | 47.8 |
| 14-Aug-09 | 1:44 | 49.8 | 63.8 | 51.0 | 46.4 |
| 14-Aug-09 | 1:59 | 48.5 | 60.2 | 50.7 | 45.5 |
| 14-Aug-09 | 2:14 | 48.3 | 56.2 | 50.5 | 45.9 |
| 14-Aug-09 | 2:29 | 50.0 | 71.0 | 51.0 | 45.5 |
| 14-Aug-09 | 2:44 | 49.5 | 61.0 | 51.5 | 45.9 |
| 14-Aug-09 | 2:59 | 51.9 | 71.5 | 54.9 | 47.2 |
| 14-Aug-09 | 3:14 | 48.4 | 56.5 | 50.3 | 46.6 |
| 14-Aug-09 | 3:29 | 49.1 | 62.8 | 50.7 | 46.6 |
| 14-Aug-09 | 3:44 | 50.3 | 58.7 | 52.7 | 47.5 |
| 14-Aug-09 | 3:59 | 49.7 | 55.7 | 51.4 | 47.9 |
| 14-Aug-09 | 4:14 | 48.8 | 59.7 | 50.1 | 47.3 |
| 14-Aug-09 | 4:29 | 49.0 | 60.8 | 50.6 | 47.0 |
| 14-Aug-09 | 4:44 | 50.3 | 63.2 | 52.7 | 47.5 |
| 14-Aug-09 | 4:59 | 50.1 | 65.8 | 52.1 | 47.5 |
| 14-Aug-09 | 5:14 | 49.8 | 65.3 | 51.4 | 47.8 |
| 14-Aug-09 | 5:29 | 49.4 | 60.0 | 51.2 | 47.6 |
| 14-Aug-09 | 5:44 | 50.8 | 62.3 | 52.5 | 48.4 |
| 14-Aug-09 | 5:59 | 54.2 | 71.1 | 55.9 | 49.4 |
| 14-Aug-09 | 6:14 | 52.1 | 62.6 | 53.9 | 50.1 |
| 14-Aug-09 | 6:29 | 54.3 | 73.6 | 55.3 | 50.5 |
| 14-Aug-09 | 6:44 | 53.5 | 62.7 | 55.5 | 51.3 |
| 14-Aug-09 | 6:59 | 55.2 | 69.1 | 57.6 | 51.5 |
| 14-Aug-09 | 7:14 | 55.3 | 66.4 | 57.7 | 51.8 |
| 14-Aug-09 | 7:29 | 57.5 | 74.5 | 58.1 | 54.7 |
| 14-Aug-09 | 7:44 | 57.3 | 75.8 | 58.2 | 52.1 |
| 14-Aug-09 | 7:59 | 55.1 | 67.7 | 58.5 | 51.9 |
| 14-Aug-09 | 8:14 | 56.4 | 70.8 | 58.2 | 52.6 |
| 14-Aug-09 | 8:29 | 53.0 | 61.2 | 54.5 | 51.5 |

APPENDIX B

Calculated Noise Levels

| RHF Fan - No Mitigation |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Frequency | 63 | 125 | 250 | 500 | 1k | 2k | 4k | 8k | Linear | dB(A) |
| Wavelength | 5.5 | 2.8 | 1.4 | 0.7 | 0.35 | 0.175 | 0.09 | 0.045 |  |  |
| A-wtg | -26.2 | -16.1 | -8.6 | -3.2 | 0.0 | 1.2 | 1.0 | -1.1 |  |  |
| Level | 88.1 | 89.9 | 90.5 | 88.1 | 83.7 | 78.4 | 72.8 | 65.0 | 95.7 | 89.3 |
| No. units | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| Level | 88.1 | 89.9 | 90.5 | 88.1 | 83.7 | 78.4 | 72.8 | 65.0 | 95.7 | 89.3 |
| Distance | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 |
| Atten | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 |
| Barrier pd | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 |  |  |
| Atten | 8.1 | 11.0 | 14.0 | 17.0 | 20.1 | 23.1 | 26.0 | 29.0 |  |  |
| Façade | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 |
| Level at receptor | 55.1 | 53.9 | 51.5 | 46.1 | 38.7 | 30.4 | 21.9 | 11.1 | 58.8 | 47.4 |
| RHF fan in enclosure, with air-side attenuator |  |  |  |  |  |  |  |  |  |  |
| Frequency | 63 | 125 | 250 | 500 | 1k | 2k | 4k | 8k | Linear | dB(A) |
| Wavelength | 5.5 | 2.8 | 1.4 | 0.7 | 0.35 | 0.175 | 0.09 | 0.045 |  |  |
| A-wtg | -26.2 | -16.1 | -8.6 | -3.2 | 0.0 | 1.2 | 1.0 | -1.1 |  |  |
| Level | 72.1 | 71.7 | 61.9 | 57.7 | 55.2 | 52.0 | 47.4 | 41.0 | 75.3 | 61.8 |
| No. units | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| Level | 72.1 | 71.7 | 61.9 | 57.7 | 55.2 | 52.0 | 47.4 | 41.0 | 75.3 | 61.8 |
| Distance | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 |
| Atten | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 |
| Barrier pd | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 |  |  |
| Atten | 8.1 | 11.0 | 14.0 | 17.0 | 20.1 | 23.1 | 26.0 | 29.0 |  |  |
| Façade | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 |
| Level at receptor | 39.1 | 35.7 | 22.9 | 15.7 | 10.2 | 4.0 | -3.5 | -12.9 | 40.8 | 22.3 |
| Condensers |  |  |  |  |  |  |  |  |  |  |
| Frequency | 63 | 125 | 250 | 500 | 1k | 2k | 4k | 8k | Linear | dB(A) |
| Wavelength | 5.5 | 2.8 | 1.4 | 0.7 | 0.35 | 0.175 | 0.09 | 0.045 |  |  |
| A-wtg | -26.2 | -16.1 | -8.6 | -3.2 | 0.0 | 1.2 | 1.0 | -1.1 |  |  |
| Level | 60.0 | 54.0 | 54.0 | 52.0 | 49.0 | 43.0 | 38.0 | 30.0 | 62.5 | 53.7 |
| No. units | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |
| Level | 64.8 | 58.8 | 58.8 | 56.8 | 53.8 | 47.8 | 42.8 | 34.8 | 67.2 | 58.5 |
| Distance | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 | 25.0 |
| Atten | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 | 28.0 |
| Barrier pd | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 |  |  |
| Atten | 8.3 | 11.2 | 14.2 | 17.2 | 20.2 | 23.3 | 26.1 | 29.2 |  |  |
| Façade | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 | 3.0 |
| Level at receptor | 31.5 | 22.6 | 19.6 | 14.6 | 8.6 | -0.4 | -8.3 | -19.3 | 32.4 | 16.3 |
| Overall Level at Receptor, Including Mitigation | 39.8 | 35.9 | 24.6 | 18.2 | 12.5 | 5.3 | -2.3 | -12.0 | 41.4 | 23.3 |