Project:	McDonald’s Restaurant – Cambridge Circus

Ref:	6961

Revision:	2 (amended for Planning)

| # Ref | Location | Service | Vol m3/s | Ext Pa | Capacity kW | Man. | Model | Weight kg | Accessories | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| S1/C1 | Roof | S1 Condenser 1 |  |  | 22 kW (cooling) 27 kW (heating) | Mitsubishi | PHUZ-RP250 YKA2 | 141 | FTC Controller per condenser. Single AHU panel mounted remote controller. Air outlet guides. | Order from Mitsubishi quoting McDonald’s corporate account. Provide drip tray. |
| S1/C2 | Roof | S1 Condenser 2 |  |  | 22 kW (cooling) 27 kW (heating) | Mitsubishi | PHUZ-RP250 YKA2 | 141 | FTC Controller per condenser. Single AHU panel mounted remote controller. Air outlet guides. | Order from Mitsubishi quoting McDonald’s corporate account. Provide drip tray. |
| S2/1 C | Roof | S2 /1 Condenser |  |  | 22 kW (cooling) 27kW (heating) | Mitsubishi | PHUZ-RP250 YKA2 | 141 | FTC Controller per condenser. Single AHU panel mounted remote controller. Air outlet guides. | Order from Mitsubishi quoting McDonald’s corporate account. Provide drip tray. |
| S2/2 C | Roof | S2 /2 Condenser |  |  | 22 kW (cooling) 27kW (heating) | Mitsubishi | PHUZ-RP250 YKA2 | 141 | FTC Controller per condenser. Single AHU panel mounted remote controller. Air outlet guides. | Order from Mitsubishi quoting McDonald’s corporate account. Provide drip tray. |
| S2/3 C | Roof | S2 /3 Condenser |  |  | 22 kW (cooling) 27kW (heating) | Mitsubishi | PHUZ-RP250 YKA2 | 141 | FTC Controller per condenser. Single AHU panel mounted remote controller. Air outlet guides. | Order from Mitsubishi quoting McDonald’s corporate account. Provide drip tray. |
| S3/1 C | Roof | S3 /1 Condenser |  |  | 19 kW (cooling) 22.4kW (heating) | Mitsubishi | PHUZ-RP250 YKA2 | 135 | FTC Controller per condenser. Single AHU panel mounted remote controller. Air outlet guides. | Order from Mitsubishi quoting McDonald’s corporate account. Provide drip tray. |
| S3/2 C | Roof | S3 /2 Condenser |  |  | 19 kW (cooling) 22.4kW (heating) | Mitsubishi | PHUZ-RP250 YKA2 | 135 | FTC Controller per condenser. Single AHU panel mounted remote controller. Air outlet guides. | Order from Mitsubishi quoting McDonald’s corporate account. Provide drip tray. |
| # Ref | Location | Service | Vol m3/s | Ext Pa | Capacity kW | Man. | Model | Weight kg | Accessories | Remarks |
| C4 | Roof | Managers office condenser |  |  | 3.6kW (cooling) 4.1kW (heating | Mitsubishi | PUHZ-RP 35 VHA4 | 42 |  | Order from Mitsubishi quoting McDonald’s corporate account. |
| C5 | Roof | Crew room condenser |  |  | 3.6kW (cooling) 4.1kW (heating | Mitsubishi | PUHZ-RP 35 VHA4 | 42 |  | Order from Mitsubishi quoting McDonald’s corporate account. |
| C6 | Roof | Door curtain condenser |  |  | 14.4 kW (heating) | Mitsubishi | PUHZ-RP140 YKA | 132 | Mod-bus Trend enable interface. Air outlet guides. | Order from Mitsubishi quoting McDonald’s corporate account |
| C7 | Roof | Door curtain condenser |  |  | 14.4 kW (heating) | Mitsubishi | PUHZ-RP140 YKA | 132 | Mod-bus Trend enable interface. Air outlet guides. | Order from Mitsubishi quoting McDonald’s corporate account |
| E1 | Roof | Kitchen Extract | 2.82 | 1200 | - | RHF Fans | BW10 500 | 400 | Std McDonald’s Spec. 2 no 5.5kW EFF1 motors. Spring AVM’s Flexible connections. Roller bearings (SN) Large cleaning/access doors at top & bottom of fan scroll. Fan scroll drain to sand trap. | Discharge R90. |

| # Ref | Location | Service | Vol m3/s | Ext Pa | Capacity kW | Man. | Model | Weight kg | Accessories | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| S1 | Lower Ground Floor kitchen ceiling void | Kitchen Supply | 2.40 | 150 | 44 kW (cooling) 54 Kw (heating) | Mitsubishi | PEA-RP 500GA | 133 | Inverter Mitsubishi controls & electrical supplies | AHU &Trend controls free issue. Order from Mitsubishi quoting McDonald’s corporate account. |
| S2/1 | Ground floor lobby ceiling void | Ground Floor Lobby Supply | 1.1 | 150 | 22 kW (cooling) 27 kW (heating) | Mitsubishi | PEA-RP 250 GA | 77 | Inverter Mitsubishi controls & electrical supplies | AHU &Trend controls free issue. Order from Mitsubishi quoting McDonald’s corporate account. |
| S2/2 | Ground floor lobby ceiling void | Ground Floor Lobby Supply | 1.1 | 150 | 22 kW (cooling) 27 kW (heating) | Mitsubishi | PEA-RP 250 GA | 77 | Inverter Mitsubishi controls & electrical supplies | AHU &Trend controls free issue. Order from Mitsubishi quoting McDonald’s corporate account. |
| S2/3 | Ground floor lobby ceiling void | Ground Floor Lobby Supply | 1.1 | 150 | 22 kW (cooling) 27 kW (heating) | Mitsubishi | PEA-RP 250 GA | 77 | Inverter Mitsubishi controls & electrical supplies | AHU &Trend controls free issue. Order from Mitsubishi quoting McDonald’s corporate account. |
| S3/1 | Lower ground floor lobby ceiling void | Lower Ground Floor Lobby Supply | 1.0 | 150 | 19 kW (cooling) 22.4 kW (heating) | Mitsubishi | PEA-RP 200 GA | 70 | Inverter Mitsubishi controls & electrical supplies | AHU &Trend controls free issue. Order from Mitsubishi quoting McDonald’s corporate account. |
| S3/2 | Lower ground floor lobby ceiling void | Lower Ground Floor Lobby Supply | 1.0 | 150 | 19 kW (cooling) 22.4 kW (heating) | Mitsubishi | PEA-RP 200 GA | 70 | Inverter Mitsubishi controls & electrical supplies | AHU &Trend controls free issue. Order from Mitsubishi quoting McDonald’s corporate account. |
| # Ref | Location | Service | Vol m3/s | Ext Pa | Capacity kW | Man. | Model | Weight kg | Accessories | Remarks |
| # S4 | Managers office | Managers office A/C unit | 0.175 |  | 3.6kW (cooling) 4.1kW (heating) | Mitsubishi | PKA-RP35 HAL | 13 | MAC397 Trend enable interface | Order from Mitsubishi quoting McDonald’s corporate account. |
| # S5 | Crew room | Crew room A/C unit | 0.175 |  | 3.6kW (cooling) 4.1kW (heating) | Mitsubishi | PKA-RP35 HAL | 13 | MAC397 Trend enable interface | Order from Mitsubishi quoting McDonald’s corporate account. |
| S6 | Entrance doors | Heat pump door curtain | 0.72 |  | 14.4kW (heating) | Mitsubishi | PHV1500R DXE HO | 67 | Mod-bus Trend enable interface | Order from Mitsubishi quoting McDonald’s corporate account |
| S7 | Patio entrance doors | Heat pump door curtain | 0.72 |  | 14.4kW (heating) | Mitsubishi | PHV1500R DXE HO | 67 | Mod-bus Trend enable interface | Order from Mitsubishi quoting McDonald’s corporate account |
| E2 |  | Toilet Extract | 0.23 | 250 |  | Helios | RR315B | 6.1 | Speed controller. |  |