- FIRE RISK ASSESSMENT

to comply with the requirements of

The Regulatory Reform (Fire Safety) Order 2005

| Company Name: Uplift Property Limited |  |  |  |  |  |  | Date: 17/03/2015 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Workplace Address: 187 Kentish Town London NW1 8PD |  |  |  |  |  |  | Contact Name: Steven Murray Contact Number: 020 7729 4189 |  |  |  |  |  |  |
| Nature of Occupancy: Construction Operations |  |  |  |  |  |  | Use of Remainder of Building: N/A |  |  |  |  |  |  |
| Construction of Building: Former town hall and restaurant with open plan ground floor, Flat roof. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Which areas of the Building are covered by this Assessment?: Areas used by Uplift Property only. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Are any areas of the Building not covered by this Assessment?: No. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| No of Floors in the Building: Two (2) |  | No of Staircases in the Building available as Exit Routes from the Workplace: Two (2) |  |  |  |  |  |  |  | No of Final Exits: Two (2) |  |  |  |
| Maximum No of Employees at Risk in the Workplace: Twenty (20) |  |  |  |  |  |  | Maximum No of other Persons at Risk in the Workplace: N/A |  |  |  |  |  |  |
| Action Required | Step 1 |  | Step 2 |  | Step 3 | Step 4 |  | Step 5 | Step 6 |  | Step 7 | Step 8 | Step 9 |
| Indicate by  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Assessor Steven Murray |  |  |  | Position Head of Health and Safety |  |  |  |  | Review Date 17/03/16 or upon building alterations or work changes |  |  |  |  |

| STEP 1 – FIRE HAZARDS | FIRE HAZARDS IDENTIFIED |
| --- | --- |
| What are the possible sources of ignition within the workplace? Consider the following: - smoking materials - faulty electrical equipment / overloaded electrical sockets - heat from processes - some chemicals (should be identified as oxidizing materials) - oxygen supplies from cylinder storage - arson | - Smoking within designated smoking area - Overloading of electrical supply - Heat from Processes |
| What sources of fuel may present a fire hazard in the workplace? Consider the following: - flammable liquid-based products (e.g. paints, varnishes, thinners, adhesives) - flammable liquids /solvents (e.g. alcohol (spirits), white spirit, methylated spirit, cooking oils, disposable cigarette lighters) - flammable chemicals (e.g. cleaning products, photocopier chemicals) - flammable gases (e.g. liquefied petroleum gas (LPG), acetylene) - displays and stands - drapes, hangings, decorations - packaging materials, stationery, advertising material - plastics and rubber (e.g. video tapes, polyurethane foam-filled furniture, polystyrene-based materials, exercise mats - upholstered seating and cushions, soft furnishings, textiles - litter and waste products (particularly shredded paper, wood shavings, offcuts, dust accumulation - fireworks and pyrotechnics | - COSHH storage - Arson - Flammable Liquids - Waste Products |
| What hazardous processes generally take place within the workplace? (e.g. welding, cutting, grinding, refuelling of vehicles, etc) | - Cutting / Grinding and Welding |
| STEP 2 – PERSONS / GROUPS AT RISK | PERSONS / GROUPS IDENTIFIED |
| Who are the persons at significant risk in the event of a fire? - employees / helpers who are unfamiliar with the premises - lone workers (e.g. cleaners) - visitors / casual users - less able persons (e.g. those with mobility, hearing or vision impairment) - unaccompanied children - emergency services (i.e. fire fighters, ambulance crews) | - Employees - Visitors - Staff |

| STEP 3 – EVALUATING THE RISKS |  |
| --- | --- |
| (a) Are all the identified hazards adequately controlled? If no, record finding in Part A | Yes |
| (b) From the hazards identified in Step 1, what is the likelihood of a fire occurring in the area being assessed? | ( or circle as appropriate): Low / Medium / High |
| (c) Taking into consideration the hazards identified in Step 1 and the persons identified as being at significant risk in Step 2, what is the likely severity of a fire that may occur in the area being assessed? | ( or circle as appropriate): Low / Medium  / High |

- PART A

| Existing significant hazards / risks that are not adequately controlled |  |
| --- | --- |
| N/A |  |
| Further Action required? Fire points to be established on all floors with smoke detectors and alarm bells to be fitted. |  |
| Action By: Site Manager | By When: As soon as works starts |

| STEP 4 - FIRE DETECTION, FIRE WARNING & EMERGENCY LIGHTING |  |
| --- | --- |
| (a) Type of fire detection system (describe): Are detectors of the right type / in appropriate locations? Does the detection system ensure that a fire warning is raised in time for all occupants to escape to a place of total safety? | None No detection, manual call points only Yes provided that a call point is activated manually |
| (b) Type of fire warning system (describe): Is the warning system sufficient for the risks involved? | M1 alarm system Yes |
| (c) Can the means for giving a warning be clearly understood throughout the whole site? | Yes |
| (d) If the fire detection and warning system is electrically powered, does it have a back-up power supply? | No Battery Powered |
| (e) Is an emergency lighting system installed? Is an emergency lighting system required? (Will the premises be used in hours of darkness?) | No No |
| (f) If installed, is the emergency lighting system independent of the main power supply? | N/A |
| (g) Have employees been informed about the fire alarm system? Do they know how to operate it? Do they know how to respond to it? | Yes Via Induction Yes Yes |
| (h) Are there sufficient numbers of Fire Action signs displayed (i.e. what to do in the event of a fire)? Have the relevant details been filled in? | Yes No |
| (i) Are there any areas, particularly unoccupied ones, where there could be a delay in detecting the start of a fire? | No |
| Further Action required? - Ensure fire extinguishers have been serviced and labelled. - Ensure the self- closing device on doors where possible. - Ensure details are completed on all fire action noticed. |  |
| Action By: Site Manager | By When: weekly |

| STEP 5 – MEANS OF ESCAPE |  |  |
| --- | --- | --- |
| (a) Are all persons in the workplace able to react quickly in the event of a fire? If not, who is affected? | Yes |  |
| (b) Is a refuge area needed to protect those unable to react quickly in the event of a fire? If so, has one been established? | No No |  |
| (c) Do exits lead to a place of safety? | Yes |  |
| (d) Are all gangways and escape routes free from obstruction? | Yes |  |
| (e) Are there enough exits? Are they in the right place and wide enough? | Yes Yes |  |
| (f) Are all escape routes / final exits correctly signed? | No |  |
| (g) Are fire doors kept closed (not ‘wedged’ in the open position)? | No |  |
| (h) Are self-closing devices on fire doors working properly? | Yes |  |
| (i) Where appropriate, do doors used for means of escape open in the direction of travel? | Yes |  |
| (j) Can all final exit doors be opened easily and immediately if there is an emergency? | Yes |  |
| Further Action required? - Ensure all fire exits are being kept clear at all times. - Ensure all fire routes are displaying fire exit signs. |  |  |
| Action By: Site Manager | By When: - One week - One week - Immediately |  |
| STEP 6 – FIRE DRILLS, WHAT TO DO IN THE EVENT OF A FIRE |  |  |
| (a) Are regular fire drills carried out? At what frequency? | Yes 6 Months |  |
| (b) Are the results of the fire drills recorded? | Yes |  |
| (c) Are Fire Marshals / Fire Wardens nominated and suitably trained? | Yes |  |
| (d) Where is the Assembly Point situated? Is it clearly identified? | Outside site entrance Yes on hoarding |  |
| (e) Do employees know what to do in the event of a fire? | Yes |  |
| (f) Do contractors / visitors to the site know what to do in the event of a fire? | Yes escorted during visit |  |
| (g) Is a roll call carried out? By whom? | Yes Fire marshals |  |
| Further action required? |  |  |
| Action By: | By When: |  |

| STEP 7 – MEANS OF FIGHTING FIRE |  |
| --- | --- |
| (a) Are sufficient fire extinguishers sited throughout the workplace? | Yes |
| (b) Are fire extinguishers: The correct type? Located correctly? Easily accessible? Mounted on a wall or stand? Appropriate signage displayed? | Yes Yes Yes Stand Yes |
| (c) Have persons likely to use the fire extinguishers been given adequate instruction and training? If yes, when? | Yes |
| Further action required? Recommend that a 2kg CO² is installed on all stands together with 6 litre water extinguishers. |  |
| Action By: Site Manager | By When: ASAP |

| STEP 8 – CHECKS, TESTING AND MAINTENANCE |  |
| --- | --- |
| (a) Are the following checked: Escape routes (recommended daily)? Fire fighting equipment (recommended weekly)? Emergency lighting system (recommended monthly)? Are the results recorded? | (at what frequency?): Daily (at what frequency?): Weekly N/A Yes |
| (b) Is the fire detection and warning system checked? At what frequency (recommended weekly)? Are the results recorded? | Yes Weekly Yes |
| (c) Have the fire detection and warning / emergency lighting systems been tested and maintained by a competent person within the last six months? Are the results recorded? | N/A N/A |
| (d) Have the fire extinguishers been tested and maintained by a competent person within the last year? Are the results recorded? | Yes Yes |
| Further action required? |  |
| Action By: | By When: |

| STEP 9 – EMERGENCY PLAN |  |
| --- | --- |
| (a) Has an emergency plan been developed? (Existing clients’ Policies contain emergency plans - is the plan being used?) | Yes Fire action notices |
| (b) Is the emergency plan displayed in prominent locations around the site? (This could be provided by fire action notices, or in more complex premises may need to be more detailed) | Yes |
| Further action required? |  |
| Action By: | By When: |