Lead Local Flood Authority – London Borough of Camden

Statutory Consultee for all Major Developments (SuDS)

| Scheme Address | Panther House, 38 Mount Pleasant The Brain Yard, 156-164 Gray's Inn Road |
| --- | --- |
| Planning Reference | 2015/6955/P |
| Size of site (as stated on application form) | 0.23 Ha |
| Date | 14.1.16 |
| Recommendation: | Subject to the provision of further requested information, approve with condition. |

Statutory Consultee for all Major developments >1ha

Description of Development:

Redevelopment of existing buildings to provide part 4 storey and part 7 storey building following partial demolition of existing Panther House and Brain Yard buildings for a mix of Class B1a (office), A1 (retail) and A3 (restaurant/cafe) uses, provision of new 7 storey building at 156-164 Gray’s Inn Road behind retained facade from existing building at 160-164 Gray’s Inn Road to provide flexible Class A1/A3 (retail/restaurant) use at ground and basement levels and 13 self contained residential units (C3) (4 x 1-bed, 7 x 2-bed and 2 x 3-bed) at upper floor levels.

Policy Requirement:

- Submit an FRA if >1ha

- Major developments to achieve greenfield run-off rates wherever feasible and as a minimum 50% reduction in run off rates.

- NPPF requires all major developments to include SuDS unless demonstrated to be inappropriate (as set out in the Ministerial Statement by the Secretary of State on 18 December 2014).

- Development should follow the drainage hierarchy in policy 5.13 of the London Plan below:

- store rainwater for later use

- use infiltration techniques, such as porous surfaces in non-clay areas

- attenuate rainwater in ponds or open water features for gradual release

- attenuate rainwater by storing in tanks or sealed water features for gradual release

- discharge rainwater direct to a watercourse

- discharge rainwater to a surface water sewer/drain

- discharge rainwater to the combined sewer

- Developments in areas known to be at risk of surface water flooding are designed to cope with being flooded.

Best practice guidance recommended within the non-statutory technical standards:

- Constrain off volumes to greenfield run off volumes for the 1 in 100 year 6 hour event.

Location of development relative to surface water flood risk:

Location of development relative to infiltration compatibility:

Documents submitted ( = YES, × = NO):

- surface water drainage statement

- drawings showing details of SuDS extent and position (appendix G of drainage strategy)

- completed drainage proforma (content is within the report)

- SuDs maintenance plan

Proposed SuDS:

As detailed in the drainage strategy, Appendix G and the proposed roof plan, the proposed SuDS include green and brown roof areas with 100mm substrate depth, and a total of 36m3 below ground attenuation storage.

Greenfield, Existing and Proposed Run off rates:

Existing run off rates

Proposed run off rates

Greenfield run off rates have not been provided

Proposed volume of water attenuated

36m3 below ground attenuation. This will reduce discharge volumes by 14% for the 1in100yr 6hour event.

Policy compliance and Further information required

Major developments to achieve greenfield run-off rates wherever feasible and as a minimum 50% reduction in run off rates.

Comment: A 50% reduction in run off rates will be achieved. The applicant has not confirmed the volume of attenuation that would be required in order to achieve greenfield run off rates, so it is not possible to assess whether this would be feasible.

Action for applicant: Confirm the volume of attenuation that would be required in order to achieve greenfield run off rates and identify potential locations where this could be located. Attenuation volumes should be maximised in order to achieve run off rates as close to greenfield rates as possible.

Developments to include SuDS unless inappropriate

Development should follow the drainage hierarchy in policy 5.13 of the London Plan

Comment: An acceptable assessment of available options in accordance with the drainage hierarchy has been completed. Green roofs and below ground attenuation are proposed.