## smartblock efficiency
SMARTBLOCK CHP EFFICIENCY
[5 empty] | Power values |  |  | Fuel consumption |  | Efficiency nett / LCV |  |  | Efficiency gross / HCV |  |  | Emissions at delivery state | [6 empty] | LCV: lower calorific value (net)
| CHP |  | Eco-design |  | Pel | Return | Pth | net | gross | electrical | thermal | total | electrical | thermal | total | Sound PL | NOx (5% O2) |  | Nox (0% O2) | CO (5% O2) |  | CO (0% O2) | HCV: higher calorific value (gross)
| type | gas | Class |  | [kW] | [°C] | [kW] | [kW] | [kW] | [%] | [%] | [%] | [%] | [%] | [%] | [dB(A)] | [mg/m³] | [mg/kWh] | [mg/kWh] | [mg/m³] | [mg/kWh] | [mg/kWh] | CONSUPTION-VALUES: EN50465:2015 7.6.1: -5%
[5 empty] | Leistungswerte |  |  | Gasverbrauch |  | Wirkungsgrad (Hi) |  |  | Wirkungsgrad (Hs) |  |  | Emissionen im Auslieferzungszustand | [6 empty] | Hi: Heizwert
| BHKW |  | Ökodesign |  | Pel | Rücklauf | Pth | Hi | Hs | elektrisch | thermisch | gesamt | elektrisch | thermisch | gesamt | Schall-DP | NOx (5% O2) |  | Nox (0% O2) | CO (5% O2) |  | CO (0% O2) | Hs: Brennwert
| Typ | Gasart | Klasse |  | [kW] | [°C] | [kW] | [kW] | [kW] | [%] | [%] | [%] | [%] | [%] | [%] | [dB(A)] | [mg/m³] | [mg/kWh] | [mg/kWh] | [mg/m³] | [mg/kWh] | [mg/kWh] | Verbrauchswerte nach EN50465:2015: -5%
smartblock | 7.5 | NG | A++ | 100% | 7.5 | 40 | 22.1 | 27.123 | 30.1065 | 27.65% | 81.48% | 109.1% | 24.91% | 73.41% | 98.32% | 40.6 | 12.1 | 12.8 | 16.8 | 12.5 | 13.5 | 17.3
|  |  |  | ~ 50% | 3.8 |  | 14 | 15.951 | 17.7056 | 23.82% | 87.77% | 111.6% | 21.46% | 79.07% | 100.5%
|  |  |  | 100% | 7.5 | 60 | 20.2 | 27.199 | 30.1909 | 27.57% | 74.27% | 101.8% | 24.84% | 66.91% | 91.75% | 40.6 | 12.1 | 12.8 | 16.8 | 12.5 | 13.5 | 17.3
|  |  |  | ~ 50% | 3.8 |  | 12.2 | 21.442 | 23.8006 | 17.72% | 56.9% | 74.62% | 15.97% | 51.26% | 67.23%
smartblock | 7,5s | NG | A+ | 100% | 7.5 | 40 | 19.3 | 27.55 | 30.5805 | 27.22% | 70.05% | 97.28% | 24.53% | 63.11% | 87.64% | 45.2 | 12.1 | 12.8 | 16.8 | 12.5 | 13.5 | 17.3
|  |  |  | ~ 50% | 3.8 |  | 12 | 16.293 | 18.0852 | 23.32% | 73.65% | 96.97% | 21.01% | 66.35% | 87.36%
|  |  |  | 100% | 7.5 | 60 | 17.4 | 27.389 | 30.4018 | 27.38% | 63.53% | 90.91% | 24.67% | 57.23% | 81.9% | 45.2 | 12.1 | 12.8 | 16.8 | 12.5 | 13.5 | 17.3
|  |  |  | ~ 50% | 3.8 |  | 10.4 | 16.245 | 18.032 | 23.39% | 64.02% | 87.41% | 21.07% | 57.68% | 78.75%
smartblock | 7.5 | LPG | A++ | 100% | 7.5 | 40 | 20.6 | 26.477 | 28.7805 | 28.33% | 77.8% | 106.1% | 26.06% | 71.58% | 97.64% | 40.6 | 12.1 | 12.8 | 16.8 | 15 | 15.9 | 20.8
|  |  |  | ~ 50% | 3.8 |  | 14.2 | 16.568 | 18.0094 | 22.94% | 85.71% | 108.6% | 21.1% | 78.85% | 99.95%
|  |  |  | 100% | 7.5 | 60 | 14.2 | 26.515 | 28.8218 | 28.29% | 53.55% | 81.84% | 26.02% | 49.27% | 75.29% | 40.6 | 12.1 | 12.8 | 16.8 | 15 | 15.9 | 20.8
|  |  |  | ~ 50% | 3.8 |  | 12.7 | 16.739 | 18.1953 | 22.7% | 75.87% | 98.57% | 20.88% | 69.8% | 90.68%
smartblock | 7,5s | LPG | A+ | 100% | 7.5 | 40 | 18.3 | 26.98 | 29.3273 | 27.8% | 67.83% | 95.63% | 25.57% | 62.4% | 87.97% | 45.2 | 12.1 | 12.8 | 16.8 | 15 | 15.9 | 20.8
|  |  |  | ~ 50% | 3.8 |  | 12.4 | 17.927 | 19.4866 | 21.2% | 69.17% | 90.37% | 19.5% | 63.63% | 83.13%
|  |  |  | 100% | 7.5 | 60 | 16.8 | 27.265 | 29.6371 | 27.51% | 61.62% | 89.13% | 25.31% | 56.69% | 81.99% | 45.2 | 12.1 | 12.8 | 16.8 | 15 | 15.9 | 20.8
|  |  |  | ~ 50% | 3.8 |  | 11.3 | 16.986 | 18.4638 | 22.37% | 66.53% | 88.9% | 20.58% | 61.2% | 81.78%
smartblock | 16 | NG | A++ | 100% | 16 | 40 | 38 | 51.68 | 57.3648 | 30.96% | 73.53% | 104.5% | 27.89% | 66.24% | 94.13% | 46 | 19.5 | 20.4 | 26.8 | 26.9 | 28.2 | 37
|  |  |  | 50% | 8 |  | 27 | 32.984 | 36.6122 | 24.25% | 81.86% | 106.1% | 21.85% | 73.75% | 95.6%
|  |  |  | 100% | 16 | 60 | 35.6 | 51.794 | 57.4913 | 30.89% | 68.73% | 99.63% | 27.83% | 61.92% | 89.75% | 46 | 19.5 | 20.4 | 26.8 | 26.9 | 28.2 | 37
|  |  |  | 50% | 8 |  | 24.7 | 32.775 | 36.3803 | 24.41% | 75.36% | 99.77% | 21.99% | 67.89% | 89.88%
smartblock | 16s | NG | A++ | 100% | 16 | 40 | 34.5 | 51.595 | 57.2705 | 31.01% | 66.87% | 97.88% | 27.94% | 60.24% | 88.18% | 50.1 | 19.5 | 20.4 | 26.8 | 26.9 | 28.2 | 37
|  |  |  | 50% | 8 |  | 23 | 31.179 | 34.6087 | 25.66% | 73.77% | 99.43% | 23.12% | 66.46% | 89.57%
|  |  |  | 100% | 16 | 60 | 31.6 | 50.977 | 56.5845 | 31.39% | 61.99% | 93.38% | 28.28% | 55.85% | 84.12% | 50.1 | 19.5 | 20.4 | 26.8 | 26.9 | 28.2 | 37
|  |  |  | 50% | 8 |  | 21.4 | 31.17 | 34.5987 | 25.67% | 68.66% | 94.32% | 23.12% | 61.85% | 84.97%
smartblock | 16 | LPG | A++ | 100% | 16 | 40 | 40.4 | 55.509 | 60.3383 | 28.82% | 72.78% | 101.6% | 26.52% | 66.96% | 93.47% | 46 | 19,5 | 20.4 | 26.8 | 26.9 | 28.2 | 37
|  |  |  | 50% | 8 |  | 27.7 | 34.276 | 37.258 | 23.34% | 80.81% | 104.2% | 21.47% | 74.35% | 95.82%
|  |  |  | 100% | 16 | 60 | 40.2 | 55.309 | 60.1209 | 28.93% | 72.68% | 101.6% | 26.61% | 66.87% | 93.48% | 46 | 19,5 | 20.4 | 26.8 | 26.9 | 28.2 | 37
|  |  |  | 50% | 8 |  | 26.8 | 34.105 | 37.0721 | 23.46% | 78.58% | 102% | 21.58% | 72.29% | 93.87%
smartblock | 16s | LPG | n. a. | 100% | 16 | 40 | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | 50.1 | 19,5 | 20.4 | 26.8 | 26.9 | 28.2 | 37
|  |  |  | 50% | 8 |  | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a.
|  |  |  | 100% | 16 | 60 | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | 50.1 | 19,5 | 20.4 | 26.8 | 26.9 | 28.2 | 37
|  |  |  | 50% | 8 |  | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a. | n. a.
smartblock | 20 | NG | A++ | 100% | 20 | 40 | 47.8 | 61.921 | 68.7323 | 32.3% | 77.2% | 109.5% | 29.1% | 69.55% | 98.64% | 45.9 | 12.3 | 14.7 | 19.2 | 22.5 | 26.8 | 35.1
|  |  |  | 50% | 10 |  | 33 | 38.39 | 42.6129 | 26.05% | 85.96% | 112% | 23.47% | 77.44% | 100.9%
|  |  |  | 100% | 22 | 60 | 44.3 | 62.197 | 69.0387 | 35.37% | 71.23% | 106.6% | 31.87% | 64.17% | 96.03% | 45.9 | 12.3 | 14.7 | 19.2 | 22.5 | 26.8 | 35.1
|  |  |  | 50% | 11 |  | 31.3 | 38.798 | 43.0658 | 28.35% | 80.67% | 109% | 25.54% | 72.68% | 98.22%
smartblock | 22 | NG | A++ | 100% | 22 | 40 | 51.2 | 67.859 | 75.3235 | 32.42% | 75.45% | 107.9% | 29.21% | 67.97% | 97.18% | 47.1 | 12.3 | 14.7 | 19.2 | 22.5 | 26.8 | 35.1
|  |  |  | 50% | 11 |  | 34.7 | 41.553 | 46.1238 | 26.47% | 83.51% | 110% | 23.85% | 75.23% | 99.08%
|  |  |  | 100% | 22 | 60 | 47 | 68.068 | 75.5555 | 32.32% | 69.05% | 101.4% | 29.12% | 62.21% | 91.32% | 47.1 | 12.3 | 14.7 | 19.2 | 22.5 | 26.8 | 35.1
|  |  |  | 50% | 11 |  | 31.3 | 41.591 | 46.166 | 26.45% | 75.26% | 101.7% | 23.83% | 67.8% | 91.63%
smartblock | 22s | NG | A++ | 100% | 22 | 40 | 49.6 | 68.562 | 76.1038 | 32.09% | 72.34% | 104.4% | 28.91% | 65.17% | 94.08% | 50.6 | 12.3 | 14.7 | 19.2 | 22.5 | 26.8 | 35.1
|  |  |  | 50% | 11 |  | 33.6 | 42.37 | 47.0307 | 25.96% | 79.3% | 105.3% | 23.39% | 71.44% | 94.83%
|  |  |  | 100% | 22 | 60 | 44.5 | 68.809 | 76.378 | 31.97% | 64.67% | 96.64% | 28.8% | 58.26% | 87.07% | 50.6 | 12.3 | 14.7 | 19.2 | 22.5 | 26.8 | 35.1
|  |  |  | 50% | 11 |  | 30 | 42.313 | 46.9674 | 26% | 70.9% | 96.9% | 23.42% | 63.87% | 87.29%
smartblock | 22 | LPG | A++ | 100% | 22 | 40 | 54.1 | 74.195 | 80.65 | 29.65% | 72.92% | 102.6% | 27.28% | 67.08% | 94.36% | 47.1 | 12.3 | 14.7 | 19.2 | 22.5 | 26.8 | 35.1
|  |  |  | 50% | 11 |  | 35.2 | 44.612 | 48.4932 | 24.66% | 78.9% | 103.6% | 22.68% | 72.59% | 95.27%
|  |  |  | 100% | 22 | 60 | 50.3 | 73.891 | 80.3195 | 29.77% | 68.07% | 97.85% | 27.39% | 62.62% | 90.02% | 47.1 | 12.3 | 14.7 | 19.2 | 22.5 | 26.8 | 35.1
|  |  |  | 50% | 11 |  | 32.8 | 44.612 | 48.4932 | 24.66% | 73.52% | 98.18% | 22.68% | 67.64% | 90.32%
smartblock | 22s | LPG | A++ | 100% | 22 | 40 | 51.4 | 72.723 | 79.0499 | 30.25% | 70.68% | 100.9% | 27.83% | 65.02% | 92.85% | 50.6 | 12.3 | 14.7 | 19.2 | 22.5 | 26.8 | 35.1
|  |  |  | 50% | 11 |  | 33.6 | 43.852 | 47.6671 | 25.08% | 76.62% | 101.7% | 23.08% | 70.49% | 93.57%
|  |  |  | 100% | 22 | 60 | 47.7 | 72.552 | 78.864 | 30.32% | 65.75% | 96.07% | 27.9% | 60.48% | 88.38% | 50.6 | 12.3 | 14.7 | 19.2 | 22.5 | 26.8 | 35.1
|  |  |  | 50% | 11 |  | 31.2 | 43.871 | 47.6878 | 25.07% | 71.12% | 96.19% | 23.07% | 65.43% | 88.49%
smartblock | 33 | NG | A++ | 100% | 33 | 40 | 73.4 | 97.651 | 108.3926 | 33.79% | 75.17% | 109% | 30.44% | 67.72% | 98.16% | 48.5 | 27.3 | 28.9 | 37.9 | 40 | 42.3 | 55.5
|  |  |  | 50% | 16.5 |  | 48.4 | 58.644 | 65.0948 | 28.14% | 82.53% | 110.7% | 25.35% | 74.35% | 99.7%
|  |  |  | 100% | 33 | 60 | 67 | 98.411 | 109.2362 | 33.53% | 68.08% | 101.6% | 30.21% | 61.33% | 91.54% | 48.5 | 27.3 | 28.9 | 37.9 | 40 | 42.3 | 55.5
|  |  |  | 50% | 16.5 |  | 43.5 | 58.843 | 65.3157 | 28.04% | 73.93% | 102% | 25.26% | 66.6% | 91.86%
smartblock | 33s | NG | A++ | 100% | 33 | 40 | 68.1 | 96.995 | 107.6645 | 34.02% | 70.21% | 104.2% | 30.65% | 63.25% | 93.9% | 54.3 | 27.3 | 28.9 | 37.9 | 40 | 42.3 | 55.5
|  |  |  | 50% | 16.5 |  | 44.8 | 58.368 | 64.7885 | 28.27% | 76.75% | 105% | 25.47% | 69.15% | 94.62%
|  |  |  | 100% | 33 | 60 | 63.6 | 97.128 | 107.8121 | 33.98% | 65.48% | 99.46% | 30.61% | 58.99% | 89.6% | 54.3 | 27.3 | 28.9 | 37.9 | 40 | 42.3 | 55.5
|  |  |  | 50% | 16.5 |  | 39.6 | 58.397 | 64.8207 | 28.25% | 67.81% | 96.07% | 25.45% | 61.09% | 86.55%
smartblock | 33 | LPG | A++ | 100% | 33 | 40 | 75.5 | 103.018 | 111.9806 | 32.03% | 73.29% | 105.3% | 29.47% | 67.42% | 96.89% | 48.5 | 27.3 | 28.9 | 37.9 | 40 | 42.3 | 55.5
|  |  |  | 50% | 16.5 |  | 49.8 | 61.931 | 67.319 | 26.64% | 80.41% | 107.1% | 24.51% | 73.98% | 98.49%
|  |  |  | 100% | 33 | 60 | 73.3 | 103.778 | 112.8067 | 31.8% | 70.63% | 102.4% | 29.25% | 64.98% | 94.23% | 48.5 | 27.3 | 28.9 | 37.9 | 40 | 42.3 | 55.5
|  |  |  | 50% | 16.5 |  | 46.4 | 62.13 | 67.5353 | 26.56% | 74.68% | 101.2% | 24.43% | 68.7% | 93.14%
smartblock | 33s | LPG | n. a. | 100% | 33 | 40 | 71.05 | 103.588 | 112.6002 | 31.86% | 68.59% | 100.4% | 29.31% | 63.1% | 92.41% | 54.3 | 27.3 | 28.9 | 37.9 | 40 | 42.3 | 55.5
|  |  |  | 50% | 16.5 |  | 44.34 | 61.142 | 66.4614 | 26.99% | 72.52% | 99.51% | 24.83% | 66.72% | 91.54%
|  |  |  | 100% | 33 | 60 | 65.76 | 103.51 | 112.5154 | 31.88% | 63.53% | 95.41% | 29.33% | 58.45% | 87.77% | 54.3 | 27.3 | 28.9 | 37.9 | 40 | 42.3 | 55.5
|  |  |  | 50% | 16.5 |  | 41.23 | 61.142 | 66.4614 | 26.99% | 67.43% | 94.42% | 24.83% | 62.04% | 86.86%
smartblock | 50 MAN | NG | A++ | 100% | 50 | 40 | 87.7 | 138.881 | 154.1579 | 36% | 63.15% | 99.15% | 32.43% | 56.89% | 89.32% | 53.9 | n. a. | n. a. | n. a. | n. a. | n. a. | n. a.
|  |  |  | 50% | 25 |  | 54 | 82.717 | 91.8159 | 30.22% | 65.28% | 95.51% | 27.23% | 58.81% | 86.04%
|  |  |  | 100% | 50 | 60 | 85.5 | 138.862 | 154.1368 | 36.01% | 61.57% | 97.58% | 32.44% | 55.47% | 87.91% | 53.9 | n. a. | n. a. | n. a. | n. a. | n. a. | n. a.
|  |  |  | 50% | 25 |  | 53.8 | 82.878 | 91.9946 | 30.16% | 64.91% | 95.08% | 27.18% | 58.48% | 85.66%
smartblock | 50 HMG (new 2016) | NG | A++ | 100% | 50 | 40 | 100.2 | 137.351 | 152.4596 | 36.4% | 72.95% | 109.4% | 32.8% | 65.72% | 98.52% | 54.8 | 26 | 27 | 35.4375 | 35 | 36.3 | 47.6437
|  |  |  | 50% | 25 |  | 66.1 | 83.325 | 92.4908 | 30% | 79.33% | 109.3% | 27.03% | 71.47% | 98.5%
|  |  |  | 100% | 50 | 60 | 90.3 | 139.223 | 154.5375 | 35.91% | 64.86% | 100.8% | 32.35% | 58.43% | 90.79% | 54.8 | 26 | 27 | 35.4375 | 35 | 36.3 | 47.6437
|  |  |  | 50% | 25 |  | 57 | 83.382 | 92.554 | 29.98% | 68.36% | 98.34% | 27.01% | 61.59% | 88.6%
smartblock | 50s HMG (new 2016) | NG | A++ | 100% | 50 | 40 | 100.2 | 142.709 | 158.407 | 35.04% | 70.21% | 105.2% | 31.56% | 63.25% | 94.82% | 56.6 | 26 | 27.5 | 36.1 | 35 | 37 | 48.5
|  |  |  | 50% | 25 |  | 66.1 | 86.982 | 96.55 | 28.74% | 75.99% | 104.7% | 25.89% | 68.46% | 94.36%
|  |  |  | 100% | 50 | 60 | 90.3 | 142.5 | 158.175 | 35.09% | 63.37% | 98.46% | 31.61% | 57.09% | 88.7% | 56.6 | 26 | 27.5 | 36.1 | 35 | 37 | 48.5
|  |  |  | 50% | 25 |  | 57 | 87.058 | 96.6344 | 28.72% | 65.47% | 94.19% | 25.87% | 58.99% | 84.86%
smartblock | 75s HMG (new 2016) | NG | A++ | 100% | 75 | 40 | 139.8 | 209.6 | 232.656 | 35.78% | 66.7% | 102.5% | 32.24% | 60.09% | 92.33% | 56.8 | 28 | 29.6 | 38.8 | 15 | 15.9 | 20.8
|  |  |  | 50% | 37.5 |  | 92.8 | 135.1 | 149.961 | 27.76% | 68.69% | 96.45% | 25.01% | 61.88% | 86.89%
|  |  |  | 100% | 75 | 60 | 125.2 | 209.4 | 232.434 | 35.82% | 59.79% | 95.61% | 32.27% | 53.86% | 86.13% | 56.8 | 28 | 29.6 | 38.8 | 15 | 15.9 | 20.8
|  |  |  | 50% | 37.5 |  | 83.7 | 135.4 | 150.294 | 27.7% | 61.82% | 89.51% | 24.95% | 55.69% | 80.64%
smartblock | X | NG | A++ | 100% | 2 | 40 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | n. a. | n. a. |  | n. a. |  | n. a.
|  |  |  | ~ 50% | 1 | 60 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | 100% | 2 | 60 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | n. a. | n. a. |  | n. a. |  | n. a.
|  |  |  | ~ 50% | 1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
smartblock | Xs | NG | A++ | 100% | 2 | 40 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | n. a. | n. a. |  | n. a. |  | n. a.
|  |  |  | ~ 50% | 1 | 60 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | 100% | 2 | 60 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | n. a. | n. a. |  | n. a. |  | n. a.
|  |  |  | ~ 50% | 1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
smartblock | X | LPG | A++ | 100% | 2 | 40 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | n. a. | n. a. |  | n. a. |  | n. a.
|  |  |  | ~ 50% | 1 | 60 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | 100% | 2 | 60 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | n. a. | n. a. |  | n. a. |  | n. a.
|  |  |  | ~ 50% | 1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
smartblock | Xs | LPG | n. a. | 100% | 2 | 40 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | n. a. | n. a. |  | n. a. |  | n. a.
|  |  |  | ~ 50% | 1 | 60 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  |  |  | 100% | 2 | 60 |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | n. a. | n. a. |  | n. a. |  | n. a.
|  |  |  | ~ 50% | 1 |  |  |  | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!