Build Design

Build Design

5, Elmfield Road

Cheltenham

Glos

GL51 9JH

01242 693047

07771867679

Basement Method Statement

3 Trinty Willoughby Road

Property Details:

3 Trinity, Willoughby Road, Hampstead

Client Information:

Mr Bradbury

1.1. This method statement provides an approach that will allow the basement design to be correctly considered during construction. The statement also contains proposals for the temporary support to be provided during the works. The Contractor is responsible for the works on site and the final temporary works methodology and design on this site and any adjacent sites.

1.2. Contact Party Wall Surveyors to inform them of any changes to this method statement.

1.3. On this development, the approach is: construct the underpin segments that will support the permanent steel work insert the new steelwork remove load from above and place it onto new supporting steelwork cast the remainder of the retaining walls that will form the perimeter of the basement.

1.4. On this project, the cantilever pins are designed to be inherently stable without lateral support to the top of the wall. However, temporary props will be provided near the head and will provide support until the concrete has gained sufficient strength. The base benefits from propping. This is provided in the final condition by the ground slab. In the temporary condition, the edge of the slab is buttressed against the soil in the middle of the property. Also the skin friction between the concrete base and the soil provides further resistance. The central soil mass is to be removed in 1/3 portions and cross propping subsequently added as the central soil ass is removed

1.5. The bearing pressures have been limited to 100kN/m2. This is standard loading for the local ground conditions and acceptable to Building Control and their approvals

1.6. The structural water proofer must comment on the proposed design and ensure that he is satisfied that the proposals will provide adequate waterproofing.

1.7. Provide engineers with concrete mix, supplier, delivery and placement methods two weeks prior to the first pour. Site mixing of concrete should not be employed apart from in small sections (less than 1m3). The contractor must provide a method on how to achieve site mixing to the correct specification. The contractor must undertake toolbox talks with staff to ensure site quality is maintained.

2. Enabling Works

2.1. The site is to be hoarded with ply board sheets, at least 2.2m high, to prevent unauthorised public access.

2.2. Licences for skips and conveyors should be posted on the hoarding.

2.3. Provide protection to public where conveyor extends over footpath. Depending on the requirements of the local authority, construct a plywood bulkhead over the pavement. Hoarding to have a plywood roof covering over the footpath, night-lights and safety notices.

2.4. Dewater:

2.4.1 There is no evidence of water entering the site at the levels to which excavation will be undertaken.

2.4.2. Should any water be discovered, the Engineer will be informed and water will be appropriately pumped from the site.

2.5. On commencement of construction, the contractor will determine the foundation type, width and depth. Any discrepancies will be reported to the structural engineer in order that the detailed design may be modified as necessary.

3. Basement Sequencing

3.1. Begin by placing cantilevered walls noted on plans. (Cantilevered walls to be placed in accordance with drawing.)

3.2. Needle and prop the walls over.

3.3.2.Dry pack to steelwork. Ensure a minimum of 24 hours from casting cantilevered walls to dry packing.Grout column bases

3.4. Excavate lightwell to front of property down to 3500mm below external ground level.

3.5. Excavate first front corner of lightwell. (drawing P01 refers)

3.6. Excavate second front corner of lightwell. (drawing P01 refers)

3.7. Continue excavating section pins to form front lightwell. (drawing P01 refers)

3.8. Place cantilevered retaining wall to the left side of front opening. After 48 hours place cantilevered retaining wall to the right side of front opening.

3.9. Needle and prop bay wall. Insert support

3.10. Excavate out first 1.2m around front opening, prop floor and

erect conveyor.

3.11. Continue cantilevered wall formation around perimeter of basement following the numbering sequence on the drawings P01

3.11.1. Excavation for the next numbered sequential sections of underpinning shall not

commence until at least 8 hours after dry packing of previous works. Excavation of

adjacent pin to not commence until 48 hours after dry packing. (24hours possible due to

inclusion of Conbextra 100 cement accelerator to dry pack mix).

3.11.2. Floor over to be propped as excavation progresses. Props to support floor to

be inserted as works progress. (drawing P01 refers)

3.12. Cast base to internal wall. Construct wall to provide support to floor and steels as works progress.

3.13. Excavate and cast floor slab

3.13.1. Excavate 1/3 of the middle section of basement floor. As excavation proceeds,

place props at a maximum of 2.5m. Locate props at a third of the height of the wall Excavate a 1/3 of the middle section of basement floor. As excavation proceeds

3.13.2. Continue excavating the next 1/3 and prop then repeat for the final 1/3.

3.13.3. Place below-slab drainage. Recommend that all drainage is encased in

concrete below the slab and cast monolithically with the slab. Placing drainage on pea

shingle below the slab allows greater penetration for water ingress.Thames Water may need to approve elements of the drainage installation

3.13.4. Place reinforcement for basement slab.

3.13.5. Building Control Officer and Engineer are to be informed 48 hours before reinforcement is ready and invited for inspection.

3.13.6. Once inspected, pour concrete.

3.14. Provide structure to ground floor and water proofing to retaining walls as required. It is recommended to leave 3-4 weeks between completion of the basement and installing drained cavity. This period should be used to locate and fill any localised leakage of the basement

4. Underpinning and Cantilevered Walls

4.1. Prior to installation of new structural beams in the superstructure, the contractor may undertake the local exploration of specific areas in the superstructure. This will confirm the exact form and location of the temporary works that are required. The permanent structural work can then be undertaken whilst ensuring that the full integrity of the structure above is maintained.

4.2. Provide propping to floor where necessary.

4.3. Excavate first section of retaining wall (no more than 1000mm wide). Where excavation is greater than 1.0m deep, provide temporary propping to sides of excavation to prevent earth collapse

(Health and Safety). A 1000mm width wall has a lower risk of collapse to the heel face.

4.4. Excavation of pins is anticipated to involve working in confined spaces and the following measures should be applied wherever applicable for deep / full depth excavations in fully enclosed pits:

o Operatives must wear a harness and there must be a winch above the excavation.

o An attendant must be present at all times, at ground level, while excavation is occupied.

o A rescue plan must be produced prior to the works as well as a task-specific risk and

method statement.

4.5. Backpropping of rear face: Rear face to be adequately propped as may be necessary in the temporary conditions with appropriate board or trench sheets, as conditions may determine.  Backpropping to extend over entire height of excavation, and can be placed in short sections as the excavation progresses.

4.5.1.If the ground is stable, backpropping can be removed as the wall reinforcement is placed and the shuttering is constructed.

4.5.2.Where trench sheets are left in a slight over spill may occur past the neighbour’s boundary wall line. Where this slight over spill is not allowed by the Party Wall Surveyors then cement particle board should be used as noted below.

4.5.3.Where soft spots are encountered, leave in trench sheets or alternatively back prop with precast lintels or sacrificial boards. If the soil support to the ends of the lintels is insufficient, then brace the ends of the PC lintels with 150x150 C24 timbers and

prop with Acrows diagonally back to the ground.

4.5.4. Where voids are present behind the lintels or trench sheeting, grout voids behind sacrificial propping. Grout to be 3:1 sand/cement packed into voids.

4.5.5.Prior to casting, place layer of DPM between trench sheeting (or PC lintels) and new concrete. The lintels are to be cut into the soil by 150mm either side of the pin. A site stock of a minimum of 10 lintels should be present to prevent delays due to ordering.

4.6. If cut face is not straight, or sacrificial boards noted previously have been used, place a 15mm cement particle board between sacrificial sheets or against the soil prior to casting. Cement particle board is to line up with the adjacent owner’s face of wall. The method adopted, to prevent localized collapse of the soil, is to install these progressively, one at a time. Cement particle board must be used in any condition where overspill onto the adjacent owner’s land is possible.

4.7. If necessary, underpins can be completed in segmental lifts (e.g. top section of wall followed by bottom section of wall).

4.7.1.Place reinforcement for retaining wall segmental lift

4.7.1.1. At lift sections, reinforcement needs to be driven in. This is to be completed by predrilling holes and inserting the reinforcement into the predrilled hole.

4.7.1.2. Underside of the wall to be cast with chamfer to allow concrete for lower lift to be cast and no packing to be required.

4.8. Excavate base. Mass concrete heels to be excavated. If soil over is unstable, prop top with PC lintel and sacrificial prop.

4.9. Visually inspect the footings and provide propping to local brickwork. If necessary install sacrificial Acrow, or pit props, and cast into the retaining wall.

4.10. Clear underside of existing footing.

4.11. Local Authority inspection to be carried out for approval of excavation base.

4.12. Place reinforcement for retaining wall base and stem. Drive H16 Bars U-bars into soil along centre line of stem to act as shear ties to adjacent wall underpin.

4.13. Site supervisor to inspect and sign off works before proceeding to next stage.

4.13.1. For pins 1, 3 and 5, inform the engineer five days before the reinforcement is ready, to allow for inspection of the reinforcement prior to casting.

4.14. Cast base. On short stems it is possible to cast base and wall at the same time. It is essential that pokers/vibrators are used to compact concrete.

4.15. Concrete Testing:

4.15.1. For first 3 pins take 4 cubes and test at 7 days

then at 14 days and inform engineer of results. Test last cube at 28 days. If cube test results are low then action into concrete specification and placement method must be

considered.

4.15.2. If results are good from first three pins, then from the 4th pin onwards take 2 cubes of concrete from every third pin and store for testing. Test one at 28 days. If result is low, test second cube. Provide results to client and design team on request or if values are below those required.

4.15.3. A record of dates for the concrete pouring of each pin must be kept on site.

4.15.4. The location of where cubes were taken and their reference number must be

recorded.

4.16. Horizontal temporary prop to base of wall to be inserted. Alternatively cast base against soil.

4.17. Place shuttering and pour concrete for retaining wall. Stop a minimum of 75mm from the underside of existing footing. It is essential that pokers/vibrators are used, hitting shutters is not considered adequate.

4.18. 24 hours after pouring the concrete pin, the gap shall be filled using a dry-pack mortar. Ram in dry-pack between the top of the retaining wall and existing masonry.

4.18.1. If gap is greater than 120mm, place a line of engineering bricks to the top of the

wall. Dry pack from the engineering bricks to existing masonry.

4.19. After 24 hours, the temporary wall shutters can be removed.

4.20. Trim back existing masonry corbel and concrete on internal face.

4.21. Site supervisor to inspect and sign off for proceeding to the next stage. A record will be kept of the sequence of construction, which will be in strict accordance with recognised industry procedures.

Extending Party Wall down and reinforced concrete underpinning

4.22 Excavate a central trench giving sufficient headroom below existing floor for working and batter back the sides as indicated on accompanying drawing.

4.22. Excavate. concrete base. If soil over unstable prop top with PC lintel and sacrificial prop.

4.23. Visually inspect the footings and provide propping to local brickwork. If necessary, Acrow or pit

props to be sacrificial and cast into the retaining wall.

4.24. Clear underside of existing footing.

4.25. Local authority inspection to be carried for approval of excavation base.

4.26. Cast reinforced concrete base

4.27. After 24hours put DPM over top of mass concrete base. It is essential that pokers/vibrators are used to compact concrete.

4.28. Place reinforcement for retaining wall. Drive H16 U-Bars into

soil along centre line of stem to act as shear ties to adjacent wall. Bottom bars of wall to be bent flush with shutter and fixed with mould release oil.

4.29. Site supervisor to inspect and sign off works for proceeding to next stage.

4.29.1. For pins 1, 3 and 5 inform the engineer 48 hours before the reinforcement is ready, to allow for inspection of the reinforcement prior to casting.

4.30. Place shuttering and pour concrete for retaining wall. Stop a minimum of 75mm from the underside of existing footing. It is essential that pokers/vibrators are used, hitting shutters is not considered adequate.

4.31. Concrete Testing:

4.31.1. For first 3 pins take 4 cubes and test at 7 days, 14 days and inform engineer of

results. Test last cube at 28 days. If cube test results are low then action into concrete

specification and placement method must be considered

4.31.2. If results are good from first three pins, then from the 4th pin onwards, take 2 cubes of concrete and store for testing from every third pin. Test one at 28 days, if result is low, test second cube. Provide results to client and design team on request or if values are below those required.

4.31.3. A record of pin poured dates must be kept on site.

4.31.4. The location of where cubes were taken and their reference number must be

recorded.

4.32. racking temporary prop to base of wall to be inserted.

4.33. 24 hours after pouring the concrete pin, the gap shall be filled using a dry-pack mortar. Ram in dry-pack between retaining wall and existing masonry.

4.33.1. If gap is greater than 120mm, place a line of engineering bricks to the top of the

wall. Dry pack from the engineering bricks to underside of the existing foundation.

4.34. After 24 hours the temporary wall shutters are removed.

4.35. Trim back existing masonry corbel and concrete on internal face.

4.36. Site supervisor to inspect and sign off for proceeding to the next stage. A record will be kept of the sequence of construction, which will be in strict accordance with recognised industry procedures.

5. Floor Support

Existing concrete ground bearing slab

5.1. The existing concrete floor to be removed to allow access to basement for excavation and removal of earth.

6. Supporting existing walls above basement

excavation

6.1. Where steel beams need to be installed directly under load-bearing walls, temporary works will be required to enable this installation. Support comprises the temporary installation of steel needle beams at high level, supported on vertical props. This will enable safe removal of brickwork below and installation of the new beams and columns.

6.1.1. The condition of the brickwork must be inspected by the foreman to determine its condition and to assess the centres of needles. The foreman must inspect upstairs to consider where loads are greatest. Point loads between windows should be given greater consideration.

6.1.2.Needles are to be spaced to prevent the brickwork above ‘saw toothing’. Where brickwork is good, needles must be placed at a maximum of 1100mmcenters. Lighter needles or Strongboys should be placed at tighter centres under door thresholds

6.2. Props are to be placed on sleepers on firm ground or, if necessary, temporary footings will be cast.

6.3. Once the props are fully tightened, the brickwork will be broken out carefully by hand. All necessary platforms and crash decks will be provided during this operation.

6.4. Decking and support platforms to enable handling of steel beams and columns will be provided as required.

6.5. Once full structural bearing is provided via beams and columns down to the new basement floor level, the temporary works will be redundant and can be safely removed.

6.6. Any voids between the top of the permanent steel beams and the underside of the existing walls will be packed out as necessary. Voids will be dry packed with a 1:3 (cement: sharp sand) dry pack layer, between the top of the steel and underside of brickwork above.

6.7. Any voids in the brickwork left after removal of needle beams can at this point be repaired by bricking up and/or drypacking, to ensure continuity of the structural fabric.

Approval

7.1. Building Control Officer/Approved Inspector to inspect pin bases and reinforcement prior to casting concrete.

7.2. Contractor to keep list of dates of pins inspected and cast.

7.3. One month after the work is completed, the contractor is to contact Adjoining Party Wall Surveyor to attend site and complete final condition survey and to sign off works.