## Sheet1
Point |  | Comments | Herrington Consulting Response | Open / Closed
1 | The climate cB2:B8hange uplift is set at 20%. The developer has stated that it has also been assessed with a 40% climate change factor and that it is suitably sized, however these calculations have not been submitted. Evidence showing that a 40% climate factor allowance can be accommodated should be provided. | Herrington’s have Calcs and will revise as necessary. | Calculations on the new model have been run for both the 20 and 40% climate change and are included in Appendix B | Closed
2 | The overall reduction in peak runoff during a 1 in 100yr storm event (+ 20% CC) achieves only a 44% reduction compared to existing stated runoff – not the 50% required under the planning condition. Excluding climate change from the results does produce the 50% reduction, but given that the climate change factor used is considered too low, this is insufficient for discharge of the condition. Use of the larger climate change factors will increase this shortfall. | Design changes to show increase in attenuation to be considered and revised calcs issued by Herringtons. | Calculations now show a 50% reduction at 100+20cc. This has been demonstarted in the report and AppendixB | Closed
3 | Thames Water has not been consulted in relation to the proposed discharge. It is essential that Thames Water are consulted and give permission for any proposed flow rates. The existing connection to the Thames Sewer has been assumed, as such this will need to be investigated and confirmed. This is relevant to any proposed surface water discharges to the combined sewer, as well as any additional foul flows generated. | LB to contact TW and procure capacity check, also carry out drainage survey and report. Al to be submitted to Herington’s for inclusion in SUDS report. | Comment added to the report to confirm the TW has been engaged: LB received verball confirmation, awaiting written confirmation. | Closed
4 | Insufficient details have been provided with regard to the positioning of the proposed SuDS features. This should be provided to show the location of the proposed SuDS features and associated pipework, including the proposed connection to the Thames Water sewer. The existing provided drawing (Figure 1) is a very high level sketch of the site, which is insufficient. | Herrington’s to enhance existing design and BDS to draw up to incorporate this. | Outline drawing has been provided in Appendix C, showing the location and the section details of the sump/pump system. | Closed
5 | The proposal is to limit discharge from the proposed building extension to 2 l/s via a 37mm orifice – given the size if the orifice there is concern this will be prone to blockages, the developer should detail how this will be mitigated. | Maintenance Methodology to be detailed by Herringtons with additional info from LB and Packaged Pump Systems. | Additional maintenance details have been added into the report, and in the proforma. Reference to a maintenance subscription which the owner is expected to comply with. | Closed
6 | The existing drainage of the site has been stated as 10 l/s, however there is no evidence supplied to support this information. Outputs from the calculations should be provided detailing the existing runoff rate, future runoff rate (with no restrictions) and also from the outputs of the designed SuDS system (including any proposed flow restrictions). | Herrington’s to enhance their Calcs. | Existing runoff characteristics have been reassessed and have been included into Appendix A of the report | Closed
7 | Insufficient detail of the proposed blue roof have been provided – this should be submitted. This should include cross sections of the proposed design, and how this will interact with the proposed green roof shown in the figures. Although 28m3 of attenuation is stated as the required storage amount, no dimensions of any SuDS features have been provided. The full dimensions of the proposed storage need to be provided. | Herringtons to sketch up designs for BDS to draw up with possible inclusion of over sized ground water tank or plastic crates over the roof, standard details of waterproofing and roof build ups to be included. | Drainage system revised (no longer a blue roof). Report has been updated and function described in the report. The storage requirements have been made clear in the report, on the outline drawing and in the calcuations. | Closed
8 | Within the calculations provided, MH10 is shown to have a 5 l/s restriction on it, however this is not discussed elsewhere, and is lower than the proposed discharge from the site during a 1 in 100 year storm, which is stated as 5.6 l/s. This discrepancy will need to be explained as this is not mentioned in the documentation. No plan is provided showing the locations of the various drainage features identified in the calculations. | New drainage drawing to be provided by BDS using drainage info from site by LB. | Outline drainage drawing has been produced based on the drainage survey. New flow restrictions have been made clear in the updated report. | Closed
9 | Exceedance events – It is stated that any excess flow from the front will likely spill to the highway, whereas to the rear it would pond behind the building. Figure 2, shows ponding is likely to occur close to the building at the rear of the property, as such a more detailed plan should be provided highlighting the areas at risk of ponding, and to provide evidence it will not impact the proposed extension or other existing features. | Herringtons to mark-up site plan showing potential ponding areas within garden boundary attenuated by extra planting? | Exceedance event description has been included, demonstrating that through localised landscaping the water will be directed away from the building, minimising the risk of internal flooding. | Closed
10 | It is not clear if the calculations provided only include the proposed drainage pipe network, or also include the blue roof attenuation. The calculations need to include all elements of the SuDS system, and their interactions. If this is already included in the calculations provided, then this should be explained in more detail. | Herringtons to explain in more details possibly within executive summary. | Calculations on the new model have been run for both the 20% and 40% climate change sceanrios and are included in Appendix B | Closed
11 | The responsibility of the SuDS system, and the maintenance of it, is stated as being the responsibility of the “owner/occupiers of the development”. This is insufficient: the proposed owners of the building should be stated, and the respective responsibilities of owners/occupiers identified. High level maintenance guidelines are included, but not who will be responsible for each action. | Owners details and PPS details to be included. | Additional details have been added into the report, Appendix E (maintenance subscription) and on the proforma. | Closed
12 | No details of drainage during construction has been provided, which should include details of how flows will be managed without impacting on surrounding drainage networks. | Construction Methodology to be drawn up by LB. | No Action Required by HC - LB provided method statement which has been included within Appendix C | Closed
13 | No details have been provided or referred to with regard to the general flood risk of the site, e.g Camden Strategic Flood Risk Assessment maps, for context. | Herrington’s to provide references to CSFRA and any other maps deemed necessary. | References have been made to Camden SFRA in the report | Closed