Annex B:  Information Required To Support Planning Application for a Commercial Kitchen.

Guildford Place, London    (BWF ref: 16841)

- Information on Premises

[Add information here on proposed type of cooking, no. of covers and ventilation system operating hours]

- The kitchen is at below street level with no accommodation above. The extract duct is exhausted at foot level in the middle of a small roundabout.

- Design Issues

- A background noise survey has been carried out by Noico. In order to address the potential noise nuisance the following actions are proposed:

  - A Noico specified silencer to comply with the councils targets

- An odour risk assessment following the methodology outlined in Annex C of Defra’s Guidance on the Control of Odour and Noise from Commercial Kitchen Exhaust Systems (Jan 2005) is attached and suggests that a “High” level of odour control is required. However, due to exhausting onto a roadway with no sensitive receptors close by and with the minimal cooking that would be happening, I would reduce this to a low level odour control required.

- In order to address the potential odour nuisance the following actions are proposed:

  - To treat the air with a pre filter and activated carbon filters with a dwell time in excess of 0.1s.

- Plans and Drawings

BWF Drawings 16841 show the proposed ventilation system. Additional information if required:

- the ductwork will be manufactured throughout in 22g galvanised steel,

- extract duct will include access hatches located in accordance with TR19 to facilitate regular cleaning

- Grease-filters

2 no. 500x400x45mm polished stainless steel baffle filters

- Manufacturer: Jasun Filtration

- Product Code: GFBES 1620

- Dimensions: 500Wx400Hx45D

- Maintenance instructions: See BWF Operations Manual and Cleaning Frequencies table attached.

- Electrostatic precipitator – not proposed

- Pre-filters – EU4 Panel Filter

- Carbon Filters – 3 no. carbon filters with a dwell time in excess of 0.1s

- UV/Ozone Odour Neutralising System – not proposed

- Cooker Hood

- Dimensions:  	1800max x 1000max mm x500mm

- Extract Airflow: 0.35m3/sec (calculated according to HVCA DW172 method 1 for the proposed cookline

- Flue Design

- A horizontal discharge from a 1000 x 220 outlet louvre with bird mesh.

- Efflux velocity at design airflow will be 3.2m/sec.

- Noise Attenuation – Noico specified silencer.

- Maintenance

- Cleaning and maintenance access panels will be provided throughout the extract system

- A recommended cleaning schedule produced by BWF (extraction system suppliers) and based upon HVCA TR/19 is attached.  Specific recommendations regarding the maintenance regime for the ESP unit will be provided once the specification of this unit has been confirmed

Attachments:

  - BW Fabrications Operation and Maintenance Manual (includes table of recommended cleaning frequencies)

  - BW Fabrications Drawings No 16841

  - Odour Risk Assessment

  - Fan Specifications:

- Extract – Systemair MUB042 400-A2 IE2

- Fan acoustic criteria

BW FABRICATIONS  April 2017