## Instructions
The UCL Mini Ska template is a self-assessment tool for use on smaller fit-out projects which are of limited scope and budget (generally up to a maximum of £2m). Examples include small-scale engineering projects, minor refurbishment work, redecoration or lighting upgrades. This version also covers smaller lab fit-out projects (e.g. individual lab fit-out, <£2m) - these requirements are ADDITIONAL to the standard Mini-Ska items. Larger fit-out projects should be assessed using the full RICS Ska methodology. Major refurbishments and new build projects generally fall under BREEAM. All relevant 'in scope' criteria must be achieved wherever practical AND unless otherwise agreed with UCL Estates.
The criteria listed should be copied directly into relevant specification and tender documentation.
For each separate Mini-Ska measure, the UPO/ project manager is responsible for confirming the following information:
In scope | Included in design | Achieved on site | Validation | References
Is the measure relevant to the scope of works for the project? | If so, have each of the requirements been fully allowed for in design and tender documentation? | (On completion of the works) Were each of the measures implemented as designed/ specified? | Provide a brief explanation of how each requirement will be/ was implemented | Provide a list of documentary evidence which can be used to confirm compliance
The lists referenced can readily be found and searched online:
Water Technology List | http://www.watertechnologylist.co.uk/
Energy Technology List | https://etl.beis.gov.uk/engetl/fox/live/ETL_PUBLIC_PRODUCT_SEARCH
BRE Green Guide | https://www.bre.co.uk/greenguide
Green Book Live | http://www.greenbooklive.com
For further information or support using this tool, please contact the UCL Sustainability Team:
Green UCL | green-ucl@ucl.ac.uk
Ben Stubbs | b.stubbs@ucl.ac.uk

## Mini-Ska
ID | Issue | Measure | Requirements | In scope? | Included in design | Achieved on site | Validation | Evidence
Have you incorporated all relevant requirements into relevant specifications/ tender documents? | [6 empty] | Please select to confirm
MS01 | Energy & CO2 | Efficient Lighting | 1. Confirm how design features have minimised the need for artificial lighting, wherever possible (e.g. by maximising daylight) 2. All new individual lamps and light fittings (luminaires) must use LED technology as standard. 3. All new general lighting systems (i.e. >20m2 and 300-500 lux) shall be designed to achieve a maximum load of 7W/m2. 4. All new installations are to be automatically controlled for daylight and occupancy, as appropriate. Spaces with natural daylight should be provided with manual on/off switches and absence detectors. 5. Where possible, include task lighting for specific lab activity as opposed to increasing lighting levels for the whole lab. 6. Information on the operation of new controls/ systems must be clearly communicated to relevant building users. | Yes | Yes |  | 1. Limited natural daylight present. 2. LED luminaires specified 3. Confirmed - new installations will have maximum load of 7W/m2. Refer to Electrical Specification for more details - light fitting schedule. 4. PIR sensor specified 5. N/A - 90% efficiency specified 6. Demonstrations to take place post completion - simple controls. | Refer to Electrical Specification and Drawings - No Spec Ref Present
MS02 | Energy & CO2 | Sub-metering | 1. Automatic monitoring and targeting (AMT) equipment is to be installed. AMT equipment comprises meters, an automatic meter reading device and analytical software. 2. Equipment must be linked to: • For heat, gas and water meters - the UCL BMS. • For electricity meters - the UCL ION Enterprise system 3. Sub-meters are to be installed for relevant zones within the fit-out area and/or high consuming energy items, as appropriate. 4. All meters must be commissioned onto UCL's BMS/ION Enterprise system prior to handover. | No
MS03 | Energy & CO2 | Connection to district heating network and chilled water systems | 1. Projects located on the main campus, or with access to a district heating network, must carry out energy modelling to ascertain the increased energy demand of the building. 2. Where feasible, the preferred option is to always connect to the district heating network for heating and an existing chilled water system for cooling. Follow the District Heating Connection standard available on UCL's Employer's Requirements page. 3. Derogations from this approach must be discussed/ agreed with the UCL energy team. | No
MS04 | Energy & CO2 | Boiler replacement | 1. The project team must carry out an options appraisal with a view to reducing life cycle energy and carbon emissions, including use of the UCL Cost & Carbon Tool. 2. New boilers are on the Energy Technology List (ETL) or meet/ exceed ETL criteria. Speak to UCL the energy team for further information. | No
MS05 | Energy & CO2 | Domestic Hot Water (DHW) | 1. Gas-fuelled DHW systems are on the Energy Technology List (ETL). 2. Electricity-fuelled DHW systems should only be used where connection to the main building system is not possible/ practical. Where required, they must have a standing heat loss better than that specified in table 5 of BS EN 15450:2007 This measure excludes electric heaters that have a storage capacity of less than 30 litres | No |  |  | New max 3kW water heater installation for wash handbasin
MS06 | Energy & CO2 | Heating, ventilation and air Conditioning (HVAC) controls | 1. Options for designing out/ minimising new mechanical plant have been considered. 2. All heating and cooling systems must be fully controlled via the Building Management System (where present). This must include the ability to change set-points and time schedules. 3. Where heating and cooling is provided by different systems in the same space this should be interlocked to prevent simultaneous operation. 4. Heating, cooling and ventilation should be controlled via a form of occupancy detection (either CO2 sensors for large spaces or presence detection for cellular offices). 5. Where appropriate (e.g. cellular offices, lab spaces) users should be provided with HVAC controls limited to +/- 1.5°C of the set point. 6. Systems should be programmed for set-points and time-schedules in line with UCL's Heating, Cooling and Ventilation policy. | Yes |  |  | Localised extract only.
MS07 | Energy & CO2 | Efficient Equipment | 1. Options for the reuse of equipment from within UCL are prioritised wherever feasible. 2. Any new equipment must meet the following energy efficiency requirements, as relevant: • White Goods: refer to UCL White Goods Procurement Policy (e.g. A+ rated fridges/ freezers) • Other small power/ plug in equipment: Energy Star rating and/ or Government buying standards • Kitchen/ catering facilities: follow CIBSE TM50 guidance | Yes | Yes |  | New smoke detector linked to existing fire detection system. | Refer to Electrical Specification and Drawings . No Spec Ref Present.
MS08 | Energy & CO2 | Energy efficient hand-dryers | NOTE - PAPER TOWEL DISPENSERS ARE NOT PERMITTED IN TOILET AREAS UNLESS FUNCTIONAL REQUIREMENTS DICTATE 1. All new electrically-operated hand-dryers are either: • 'Biodrier Eco' (www.biodrier.com); or • have equivalent energy performance and noise rating; or • have been awarded a carbon reduction label by The Carbon Trust. | No | No
MS09 | Materials | Timber | 1. 100% of timber used is from at least one of the following sources: • is reclaimed; or • all new timber must be supplied with a Chain of Custody (CoC) from one of the following forest certification schemes only: - Forest Stewardship Council (FSC) - Programme for the Endorsement of Forest Certification (PEFC) - Grown in Britain certification (GiB) | Yes | Yes |  | FSC certified timber specified. | Refer to Door Specification - Materials & Workmanship Section L20.
MS10 | Materials | Flooring | 1. Options for reuse or recycling of existing floor finishes must be prioritised, including through supplier take back schemes where available. 2. All new floor coverings must meet at least one of the following criteria: • are reused • if new, are manufactured with 25% recycled content for hard flooring or 50% recycled or renewable/natural content for soft flooring • have an A or A+ rating in BRE’s The Green Guide to Specification/ Green Book Live database • carpets are installed as part of a manufacturer’s recycling or ‘take back’ scheme and are labelled accordingly 3. New flooring must be recyclable (designed for deconstruction with components that can be recycled) 4. In addition, ALL timber, must meet the criteria of good practice measure MS08 Timber. | Yes | Yes |  | Existing floor covering not fit for purpose. Vinyl to be installed throughout - to suit existing nursery specification to maintain continuity. | Refer to Schedule of Work Item 6.00.
MS11 | Materials | Furniture (e.g. workstations, tables, chairs, storage units) | 1. All reasonable options for reuse in situ have been exhausted 2. Adequate arrangements are made for the storage or reuse of any redundant, but reusable, items 3. Projects must check existing UCL inventory with a view to reusing items from storage/ other projects 4. Any new items meet at least one of the following criteria • the company manufacturing the products is certified under the Furniture Industry Sustainability Programme (FISP) scheme; • are manufactured with at least 80% recycled content and 100% recyclable content, designed for deconstruction with components that can be recycled, measured by mass. • have been awarded the EU Ecolabel 5. In addition, ALL timber, must meet the criteria of good practice measure MS08 Timber. | Yes |  |  | UCL Estates to procure.
MS12 | Materials | Other Materials: (Please specify) | Any material used as part of the fit-out should be one of the following: • reused or reclaimed; • contain at least 80% recycled or recyclable content; • have an A or A+ rating in BRE’s The Green Guide to Specification; • have an A or A+ rating in BRE’s Green Book Live database; or • are supplied with an Environmental Product Declaration (EPD), written in accordance with ISO 14025 standards. • is supplied with a cradle to cradle certificate (silver-platinum) | Yes |  |  | Gyproc WallBoard can be recycled through British Gypsum’s dedicated Plasterboard Recycling service. End of life recycling rate of 17%. Kitchen fittings are stainless steel - widely recycled.
MS13 | Waste | Construction waste planning and recycling | 1. Waste minimisation and management must be approached in accordance with the waste hierarchy (i.e. in order of priority: reduce - reuse - recycle - recover - dispose) 2. All projects must have clear plans for waste management with a view to minimising overall waste levels AND waste to landfill. For any projects involving extensive strip out or furniture replacement, this should involve a documented waste audit/ inventory of items to be provided to the UCL Sustainability Team and Waste Manager, carried out at project inception. 3. Projects generating larger quantities of waste (QUANTITY REQUIRED) or >2 months in duration must prepare a resource (site waste) management plan prior to the construction phase Waste reports must be recorded and broken down by waste steam and show that at least 90% of waste produced on site is diverted from landfill. Note: For projects less than 2 months in duration, a final waste report will be accepted. For those longer than 2 months, please provide on-going waste reports showing compliance with the below: At least 90% of all construction and demolition (C&D) waste is: • reused; • recycled; or • diverted from landfill. | Yes | Yes
MS14 | Waste | Operational waste facilities | Any projects leading to variations in waste types/ volumes must provide adequate new facilities, including bins approved by the UCL waste manager to help maximise segregation and recycling rates. Risk assessments must be completed for any new waste streams. | No
MS15 | Water | Water-efficient sanitary equipment | • WCs have an effective flush volume of 4.5 litres or less (existing systems should be retrofitted where practical) • Flow rate on taps is limited to 6 litres/minute up to a pressure of 5 bar (through new taps or retrofitting flow control devices) AND/OR Automatic shut-off taps are installed. Each time the tap is activated the water only flows for a maximum of 20 seconds. • Flow rate to showers is limited to 8 litres/minute up to a pressure of 5 bar (+/– 0.2 bar) • A control system to isolate the water supply when the washrooms are unoccupied is specified and installed. This usually comprises a solenoid valve and occupancy sensor. The shut-off system only needs to be applied to the cold water supply to taps, WCs and urinals. | Yes | Yes |  | Taps: Factory fitted 3.8 litres per minute flow regulator. 1.9 litres per minute Eco spray outlet supplied. $.6 / 6 litre flush | Refer to Mechanical Specification. No Spec Reference Present.
MS16 | Wellbeing | Daylight and glare control | • Design space to maximise natural daylight opportunities, as appropriate (e.g. consider specailst functions, photo-sensitive materials etc). • Occupant-controlled window coverings (typically blinds or screens) must be fitted to the external windows and atria that receive sunlight directly or indirectly. • Coverings are to be designed to provide optimum glare control and allow the best possible retention of views out. • Fabric screens, where specified, should have a visual light transmittance (VLT) of less than 10%. Use black-out blinds where necessary. | Yes | Yes |  | Natural daylight limited - see above. Blinds fitted to all windows and exterrnal doors (due to nursery function). | Refer to Schedule of Work Item 8.01.
MS17 | Wellbeing | Outside views | • Where feasible, the layout of permanent workstations must be planned to allow for an outside view that is within seven metres of external windows and visible within 65 degrees rotation from the normal working position | No | No
MS18 | Wellbeing | Paints & finishes | • Low or zero volatile organic compound options must be specified • Paints & varnishes • Wood panels (e.g. MDF, plywood, acoustic board etc) • Wood flooring • Textile and laminated floor covering • Ceiling tiles • Flooring adhesives • Wall coverings | Yes | Yes |  | Water-based paints specified - low E specified throughout. | Refer to Schedule of Work Item 10.00 and M&W Section M50.
Further guidance on relevant standards is available here.
MS19 | Pollution | Refrigerants | 1. Refrigerants used in systems must have an Ozone Depleting Potential (ODP) of 0 (e.g. HFCs), unless otherwise agreed. (e.g. where the value of the cooling systems is under £10,000 in which simply the refrigerants selected must be stipulated.) R32 will meet this requirement. | No
MS20 | Other | Occupant guidance & instructions (Building User Guide) | 1. Written operational guidance must be provided to inform and guide the building users and non-technical building managers on the operation and environmental performance of the space, with a view to optimising energy efficiency... and how to ensure a high level of environmental operation on a day to day basis. This should be a light-weight tool and separate from O&M's. The scope of guidance will be dependent on project size or complexity, but must be in a non-technical, accessible format (e.g. appropriate signage, laminates adjacent to building controls, desk top guides, mobile apps or electronic guides). | Yes | Yes |  | Included on Handover procedure. | Refer toMechanical Specification.
MS21 | Other | Commissioning | • New systems are commissioned or existing systems are recommissioned in accordance with CIBSE & BSRIA guidance • Provide updated commissioning records/documentation to confirm that the building has been fine-tuned and seasonal commissioning of complex equipment has been undertaken. | Yes | Yes |  | Included on Handover procedure. | Refer toMechanical Specification.
Yes | Yes
No | No
N/A
Please select to confirm
Yes
No
Note on D2: All relevant requirements must be accounted for. Derogations to be agreed with UCL Sustainability.
Note on D4: Where changes/ upgrades are being made to lighting systems:
Note on D5: Where major work to mechanical, electrical or water supply systems is being carried out:
Note on D6: For projects involving major heating/cooling system modifications:
Note on D7: Where boilers are being upgraded or replaced: UCL Cost & Carbon Tool is available at: http://www.ucl.ac.uk/greenucl/resources/construction
Note on D8: Where dedicated DHW systems are being upgraded or replaced (i.e. separate from space heating): A copy of the relevant requirements from BS EN 15450:2007 is available in the full Ska HE Standard, available at:http://www.rics.org/uk/knowledge/ska-rating-/ska-he/
Note on D9: Where HVAC systems are being upgraded or replaced: UCL Heating, Cooling and Ventilation Policy available at: www.ucl.ac.uk/greenucl/heating
Note on D10: Where new electrical/ electronic equipment is required: A copy of the UCL White Goods Procurement Policy is available from the Sustainability Team: green-ucl@ucl.ac.uk
Note on D12: Where timber or timber-derived products are specified:
Note on D13: Where floor finishes are being upgraded or replaced:
Note on D14: Where furniture items are planned to be replaced:
Note on D15: For projects involving significant use of other materials:
Note on D16: All projects:
Note on D17: All projects:
Note on D18: Where sanitary equipment is being upgraded or replaced:
Note on D19: For occupied spaces with workstations and windows:
Note on D20: For all occupied spaces with eye-level windows:
Note on D21: Where the internal fit-out includes any of the products/ materials listed here:
Note on D23: Where cooling systems are being specified, upgraded or replaced:
Note on D24: Where building services or AV equipment has been provided or upgraded:
Note on D25: For all projects involving the specification, upgrade or replacement of building services:
Note on E2: Is this measure relevant to the scope of works for the project?
Note on F2: Have each of the requirements been allowed for in design and procurement documentation?
Note on G2: Were each of the measures implemented as designed? Confirm on project completion
Note on H2: Provide a brief explanation of how each requirement will be/ was implemented
Note on I2: Provide a list of documentary evidence which can be used to confirm compliance and state where this can be found

## Ska-Labs
ID | Issue | Measure | Requirements | In scope? | Included in design | Achieved on site | Validation | Evidence
Have you incorporated all relevant requirements into relevant specifications/ tender documents? | [6 empty] | Please select to confirm
L01 | Ventilation | Air change selection | • Systems should modulate to satisfy F/C demand, occupancy & min vent rates for lab, whichever is the higher. • Note CIBSE Guide B recommends a broad range of 6-15 ACH for laboratories. • Please indicate what ACH has been selected, and provide rationale.
L02 | Ventilation | Air change reduction | • One of the two following options for ACH savings should be employed: 1. Demand driven ventilation using CO2 sensor if the occupancy ventilation rate is higher than other ventilation rate requirements. 2. Reducing air change rates and room temperature range via night time setbacks during unoccupied hours. Note it is extremely rare for any building to require 24/7 ACH which assume full occupancy. Also note that HVAC zoning may be required to achieve maximum savings from setbacks (for e.g. between offices and labs).
L03 | Ventilation | Air temperature range | • Consider the impact of incoming equipment heat load, for e.g. freezers, and ensure controls or sensors are not near heat outputs. Passive cooling strategies must be optimised for such spaces. ULT freezers should not exceed environmental temperatures of 22-25C. • Functional requirements such as close control are exempt from this measure.
L04 | Ventilation | Make up air | • Where ventilation modifications are made to building-wide ventilation function, undertake a rebalancing exercise of the full building's ventilation system.
L05 | Ventilation | Negative pressure | • Labs should have an inward air trend for containment requirements - consider cascading supply air from adjacent office and write up areas.
L06 | AHUs | Heat recovery | • Recover energy from exhaust with corrosion resistant heat recovery coils. • Ensure fresh air is at a higher pressure than exhaust for plate heat exchangers. • Ensure intake is at an appropriate distance from exhausts so that there is no recycling of polluted/ stale air.
L07 | Equipment loads | Electrical consumption | • Any equipment with 3-phase power, excess cooling/heating, water or drain, or specialist requirements should be notified to UCL Sustainability/ Estates. • Consult with users about new equipment - consider options for sharing/ alternatives nearby. • Laboratories which are purchasing generic new equipment should perform whole-life costing particularly for ULT freezers, -20C freezers, safety cabinets, drying cabinets, and autoclaves.
L08 | Equipment loads | Location/extraction | • Capture heat at source, or remove high heat emitting equipment from laboratory environment. Consider installing PCR machines and freezers in dedicated area using natural vent to remove heat gains, though ensure there is sufficient back-up cooling for warm conditions. Equipment rooms such as for ULT freezers should not exceed 22C. Good practice is to share heat emitting equipment in dedicated rooms/share resources between labs.
L09 | Fume Cupboard selection and operation | Air Flow | • VAV fume cupboards should be installed where they will lead to overall energy reductions. Consideration must be made for room ACH requirements and heating/cooling. • Any variations in required maintenance should be communicated to UCL Estates, H&S, and Sustainability. Indicate why VAV has not been selected if so.
L10 | Fume Cupboard selection and operation | Air Flow | • Ensure sufficient containment at the lowest face velocity for fume cupboards in compliance with test requirements of BS EN 14175 by targeting face velocities of 0.3-0.5ms for normal activities and where risk assessment permits. • Low-flow (0.3-0.4ms) must be validated via containment testing prior to usage. Ensure there has been consideration for possible disturbances of flow.
L11 | LEV selection and operation | Air Flow | • Provide evidence that possible increases in future extract requirements to suit different activities have been considered, and an allowance for this has been included in the sizing of the ventilation system. • Re-circulating safety cabinets have been prioritised over ducted, and rationale for ducted has been communicated. • Any replacement of ducted with re-circulating models has taken into consideration increased heat loads as well as possible variances in decontamination procedures.
L12 | Fume Cupboard selection and operation | Energy efficiency | • Maximum height of 400mm for fume cupboards. Sashes can be raised higher to permit access for setting up, etc.
L13 | Fume Cupboard selection and operation | Energy efficiency | • Provide separate ventilated storage for chemicals to allow fume cupboards to be turned-off out of hours.
L14 | Fume Cupboard selection and operation | Energy efficiency | • Provide controls to switch fume cupboards to a setback condition in periods of non-use or off when out of normal working hours, with the option of locally overriding this where experiments are run overnight or during weekends.
L15 | Fume Cupboard selection and operation | Energy efficiency | • Install passive infrared monitoring to set back air volume and/or automatic sash closure in absence of users.
L16 | Fume Cupboard selection and operation | Monitoring and operational guidance | • Provide a user guide that includes operation advice on reducing energy usage, this should be delivered/defined with the compulsory training outlined in HSE CGS 201. • Ensure all local controls and relevant mechanics (what closing the sash does, possible alarm triggers, what all lights/buttons/symbols do, etc.) are clearly described and written for current and future users
L17 | Water | Sink sizing and necessity | • Recirculating chillers instead of taps or sinks must be prioritised. • Reduce sink sizes where possible to reduce volume of 'soaking' for glassware, though consider largest glassware to be washed.
L18 | Waste | Appropriate Waste Disposal Routes | • Provide receptacles and space for minimum 3 waste streams, with non-hazardous waste streams separated physically from hazardous/clinical. • Clear labelling (available from the sustainability team) must be installed.
L19 | Ventilation | Air change rate in BSU | • Reduce BSU ACH where solely IVCs have been installed, and with Home Office approval As a guide: ACH should be 12 (+/-2 ACH) in facilities with IVC and rooms where animals are not exposed.
| Please select to confirm | Yes
| Yes | No
| No | N/A
Note on D2: All relevant requirements must be accounted for. Derogations to be agreed with UCL Sustainability. Note that Labs requirements are additional to basic Mini-Ska items
Note on E2: Is this measure relevant to the scope of works for the project?
Note on F2: Have each of the requirements been allowed for in design and procurement documentation?
Note on G2: Were each of the measures implemented as designed? Confirm on project completion
Note on H2: Provide a brief explanation of how each requirement will be/ was implemented
Note on I2: Provide a list of documentary evidence which can be used to confirm compliance and state where this can be found