|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Matthew Dempsey, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 20 January 2020 |
| Re: | 112 Great Russell Street London WC1B 3NQ |
| Proposal: | Installation of 3 x condenser units, at first floor level behind parapet adjacent to existing plant. 2 x to Great Russell Street and 1 x to Bedford Avenue, relocated from basement level (Retrospective). |
| Reference: | 2019/1289/P |
| Key Points: | The proposals are acceptable in environmental health terms |

I have taken a look at the submitted acoustic assessment which has proposed sufficient levels with specified noise mitigation in report revised dated 4th November 2019. Therefore I do not have any objections to the installation and suggest the following condition should you be mindful to grant the application.

- Where noise emitted from the proposed plant and machinery will not contain tones or will not be intermittent, the ’A’ weighted sound pressure level from the plant and machinery (including non-emergency auxiliary plant and generators) hereby permitted, when operating at its noisiest, shall not at any time exceed a value of 10 dB below the minimum external background noise, at a point 1 metre outside any window of any residential and other noise sensitive property, unless and until a fixed maximum noise level is approved by the Council. The background level should be expressed in terms of the lowest LA90, 15 mins during the proposed hours of operation. The plant-specific noise level should be expressed as LAeqTm, and shall be representative of the plant operating at its maximum.

- Where noise emitted from the proposed plant and machinery will contain tones or will be intermittent, the ’A’ weighted sound pressure level from the plant and machinery (including non-emergency auxiliary plant and generators) hereby permitted, when operating at its noisiest, shall not at any time exceed a value of 15 dB below the minimum external background noise, at a point 1 metre outside any window of any residential and other noise sensitive property, unless and until a fixed maximum noise level is approved by the Council. The background level should be expressed in terms of the lowest LA90, 15 mins during the proposed hours of operation. The plant-specific noise level should be expressed as LAeqTm, and shall be representative of the plant operating at its maximum.

- Following installation of the plant and equipment, you may apply in writing to the City Council for a fixed maximum noise level to be approved. This is to be done by submitting a further noise report confirming previous details and subsequent measurement data of the installed plant, including a proposed fixed noise level for approval by the City Council. Your submission of a noise report must include:

(a) A schedule of all plant and equipment that formed part of this application;

(b) Locations of the plant and machinery and associated: ducting; attenuation and damping equipment;

(c) Manufacturer specifications of sound emissions in octave or third octave detail;

(d) The location of most affected noise sensitive receptor location and the most affected window of it;

(e) Distances between plant & equipment and receptor location/s and any mitigating features that may attenuate the sound level received at the most affected receptor location;

(f) Measurements of existing LA90, 15 mins levels recorded one metre outside and in front of the window referred to in (d) above (or a suitable representative position), at times when background noise is at its lowest during hours when the plant and equipment will operate. This acoustic survey to be conducted in conformity to BS 7445 in respect of measurement methodology and procedures;

(g) The lowest existing LA90, 15 mins measurement recorded under (f) above;

(h) Measurement evidence and any calculations demonstrating that plant and equipment complies with the planning condition;

(i) The proposed maximum noise level to be emitted by the plant and equipment.

Reason: To safeguard the amenities of the adjoining premises and the area generally in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017.

Plant or equipment and ducting at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration.

If you have any queries, please do not hesitate to contact me.

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967652382