|  | S |
| --- | --- |

ENVIRONMENTAL HEALTH

SUPPORTING COMMUNITIES

| To: | Mark Chan, Planning Officer, Development Management, 5 Pancras Square N1C |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 09 July 2020 |
| Re: | 196-198 Haverstock Hill London NW3 2AG |
| Proposal: | Relocation of plant equipment and installation of 2x condenser units and extract fans and associated ductwork to roof level of rear extension |
| Reference: | Planning application ref. 2020/1462/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

The site is bounded by Haverstock Hill (A502) to the west, Haverstock Hill to the south, and a combination of residential and commercial properties in the general locality.

The closest noise sensitive receiver to the proposed installation location has been identified as being a first-floor residential window of 196 Haverstock Hill, located at varying distances from the proposed plant locations

It is understood that the proposed plant installation is comprised of the following units:

- 2No. Mitsubishi Electric PUMY-P200YKM Air Conditioning Unit

- 2No. Mitsubishi Electric PUHZ-ZRP7VHA2 Air Conditioning Unit

- 1 No. Tecool E100H Cold Room Condenser

- 1 No. Systemair MUB/T 560 D4 IE2Extraction Fan

- 1 No. Systemair ARSileo 450-E4 Supply Fan

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, Camden Council’s Local Plan, version June 2017 and BS 4142:2014.

In order to achieve the specific sound level and subsequent rating level calculated the submitted assessment appropriate noise control strategy should be adopted.

The submitted report uses manufacturer’s noise data of proposed plant units to obtain specific and rated noise levels at the nearest noise sensitive receiver in accordance with British Standard BS4142:2014 for compliance with London borough of Camden requirements.

The report reasonably concluded that noise emissions from the proposed plant units would not have an adverse impact on the nearest residential receivers provided that the noise control measures specified are followed and therefore I am satisfied that the submission is satisfactory in environmental health terms.

Suggested conditions:

The external noise level emitted from plant, machinery or equipment with specified noise mitigation at the development hereby approved shall be lower than the lowest existing background noise level by at least 10dBA, by 15dBA where the source is tonal, as assessed according to BS4142:2014 at the nearest and/or most affected noise sensitive premises, with all machinery operating together at maximum capacity

Reason: To safeguard the amenities of neighbouring noise sensitive receptors in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017.

Vibration

Suggested conditions:

Before the use commences, plant shall be provided with acoustic isolation, and anti-vibration measures. All such measures shall thereafter be retained and maintained in accordance with the manufacturers' recommendations.

Reason: To prevent the transmission of noise and vibration throughout the building and or into any neighbouring premises, thus safeguarding the amenities of the [adjoining] premises [and the area generally] in accordance with the requirements of policies A1, A4 of the London Borough of Camden Local Plan 2017.

If you have any queries, please do not hesitate to contact me.

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967652382