## Case details
Energy Memo: GLA Consultation
Case details
Date of first review: | 13/01/2020
Case Name: | Royal Throat, Nose and Ear Hospital Site
Case Number: | 2020/6909
Case Officer: | Areena Berktold
London Borough: | Camden
Application Type (Outline/Hybrid/Detailed): | Detailed
Applicant: | 330 Grays Inn Road Ltd
Energy Consultant: | XCo2
Document Title: | Energy Statement
Document Date: | 2020-11-01
Development proposals
Use | Floorspace/Number of units
Dwellings | 44
Office | 13,275 m2
Hotel | 9,247 m2

## Energy Comments
Comment No. | GLA Stage I | Applicant's Stage I response | GLA Post Stage I response | Applicant's Post Stage I response
| Date: 13/01/2021 | Date: 25.02.2021 | Date: | Date:
General compliance comments
1 | The energy strategy is generally compliant with the London Plan policies however, the applicant is required to submit the additional information, which has been requested below. | N/A
2 | For the purposes of this assessment, the applicant will be estimating the CO2 emission performance against London Plan policies using the SAP 10 emissions factors. This is supported. | N/A
3 | The applicant has submitted the GLA’s Carbon Emission Reporting spreadsheet, which has been developed to allow the use of the updated SAP 10 emission factors alongside the SAP 2012 emission factors. Please can they also submit the excel file for this spreadsheet. | Provided, see attached file.
Be Lean
4 | Based on the information provided, the domestic element of the proposed development is estimated to achieve a reduction of 12.6 tonnes per annum (17%) in regulated CO2 emissions compared to a 2013 Building Regulations compliant development. The applicant is require to reduce the g-value inline with comments on overheating. Should this have an impact on the ability to meet the 10% energy efficiency saving target then further measures should be investigated for the domestic element. | The Energy Statement calculations have taken into consideration the g-values reduction recommended by the Overheating Assessment. See additional response on point 7.
5 | Based on the information provided, the non-domestic element of the proposed development is estimated to achieve a reduction of 62.1 tonnes per annum (10%) in regulated CO2 emissions compared to a 2013 Building Regulations compliant development. The applicant should note that the London Plan includes a target of a minimum 15% improvement on 2013 Building Regulations from energy efficiency which applicants will be expected to meet. The applicant should therefore model additional energy efficiency measures to meet the EE target. The applicant should confirm if WWHRs are to be included within the Hotel as this is expected to have a real world benefit and should be proposed if not already. | For the whole development, XCO2 coordinated with the design team to explore all strategies to reduce carbon emissions. Fabric u-values have been reduced as far as was deemed feasible, glazing areas adequately sized and low g-value proposed to reduced cooling reliance, all internal lighting to be low-energy and the mechanical ventilation to have heating recovery. Overall the heating and cooling demands have been extensively reduced. As mentioned in the submitted Energy Statement, the implementation of waste water heat recovery (WWHR) systems was evaluated for the whole development and only considered suitable for the Hotel building due to its high domestic hot water demand, so it is already proposed.
6 | The applicant has considered the estimated energy costs to occupants and has outlined how they are committed to protecting the consumer from high prices. | N/A
Overheating
7 | The results of the Dynamic Overheating Analysis, using the CIBSE TM59 methodology, demonstrate that DSY 1 compliance is achieved assuming a g-value of 0.5/0.7 and air tempering within the proposed MVHR Unit. The applicant should confirm that any required blinds will be included in the base build and demonstrate that the blinds do not interfere with the effective opening area of windows. The applicant is required to investigate and adopt further passive measures (in line with the Cooling Hierarchy) to avoid the risk of overheating now and under future climate scenarios. The g-value assumption is considered high for domestic development and may be increasing the reliance on air tempering. This is not supported and the g-values should be reduced. The applicant should provide further details on the constraints for natural ventilation and reference the relevant supporting reports. They should confirm if window openings are being proposed and should demonstrate that, if a natural ventilation strategy was relied on rather than a tempered air solution, that Tm59 compliance could be achieved. | Internal blinds will be provided in the base build and the detail deisgn will take into consideration the blinds' operation so they not interfere with the effective opening of windows. The overheating risk mitigation strategy has followed the cooling criteria and passive measures have been extensively explored to reduce the risk of overheating now and under future climate scenarions and minimise the reliance in air tempering. The g-values have only been reduced to 0.4 in the south facing facade to reduce the solar gains. For the north facade was increased to 0.7 to improve daylight and reduce energy demand. Natural ventilation is not to be relied upon based on air quality and acoustic requirements. Therefore no opening of windows is proposed, aside from purge ventilation requirements. Therefore we have no provided results for the scheme depending on natural ventialtion for overheating. Please refer to the Acoustic and Air Quality reports submitted in support of the application.
8 | The area weighted average (MJ/m2) and total (MJ/year) cooling demand for the actual and notional building has been provided and the applicant has demonstrated that the actual building’s cooling demand is lower than the notional. | N/A
Be Clean
9 | The applicant has carried out an investigation and there are no existing or planned district heating networks within the vicinity of the proposed development. They have contacted relevant stakeholders including the borough energy officer who have confirmed that there are currently no plans to extend the network closer than teh current 400m seperation identified. They applicant should also confirm if they have contacted Argent the network operator to confirm if there is any business interest in a connection to the proposed development. | XCO2 liaised with Camden energy officer (via Gerald Eve) who advised that Argent DHN only reaches as far as Pancras Square, so it is much further than 400m to the 330 Gray’s Inn Road site. Therefore, Argent was not contacted as connection to the DHN was not deemed viable from the outset.
10 | The applicant has provided a commitment that the development is designed to allow future connection to a district heating network. Drawings demonstrating how the site is to be future-proofed for a connection to a district heating network should be provided. This should include a single point of connection to the district heating network. | The developent is proposed to be served by a communal energy centre shared by all users (hotel, office, gym and residential). Please see heating schematic attached showing allowance for a single point of connection to the future district heating network.
11 | The applicant is proposing a communal heat network supplied by a centralised energy centre. It has been confirmed that all apartments and non-domestic building uses will be connected to the heat network. A drawing showing the route of the heat network linking all uses on the site has been provided alongside a drawing indicating the floor area, internal layout and location of the energy centre. The applicant should clarify why the 80oC flow temperatures are reqeuired as this is seen as a barrier to ASHP only solutions. | The developent is proposed to be served by a communal energy centre shared by all users (hotel, office, gym and residential). Energy Centre and Building Heat Network route drawings attached. The 80°C LTHW flow temperature is required to feed the commercial calorifers' coils. The standard sizing of the calorifiers' coils is based on 80/60 LTHW temperatures, as per manufacturer's literature. The residential heat network is designed to operate at a 70°C flow temperature, a blending valve is proposed within the energy centre. Note that the system utilises electric boilers for LTHW temperature top-up of the commercial domestic hot water and the residential heat network circuits (70°C+). These circuits are proposed to be pre-heated via the 4-pipe ASHP system, therefore maximising the amount of heat that can be generated efficiently via ASHPs. The commercial areas (hotel, office and gym) space heating is proposed to be generated 100% via ASHPs. In addition, the 4-pipe ASHP system offers heat recovery capacity between the residential and commercial areas.
Be Green
14 | The applicant is proposing to install 24.70kWp of Photovoltaic (PV) panels equating to circa 130 m2 of net PV area and 18,784 kWh of electricity generation. A detailed roof layout has been provided demonstrating that PV has been sited on green roof areas that are not overshaded. The applicant should confirm if there is potential to include PV ontop of plant and core areas. The on-site savings from renewable energy technologies should be maximised regardless of the London Plan targets having been met. | The PV area proposed has been discussed in detail with the design team and maximised to the extent possible. PV cannot be added on top of plant as they would obstruct the discharge air path. Adding PV over the generators and the lift overruns was considered. However, since the lift overruns will be quite small, the number of panels will be small and gaps around the panels will be quite large. This is not expected to be very useful in terms of contributions to savings and will not provide a valuable cost benefit. Any PV placed around the generators will need to be built on an independent frame and coordinated around the exhaust, which increase the complexity and cost when compared to low savings gained.
15 | Heat pumps are being proposed in the form of a (centralised) hybrid system with ASHP and electric boilers. Further information on the heat pumps should be provided including: b. Details of how the Seasonal Coefficient of Performance (SCOP) and Seasonal Energy Efficiency ratio (SEER) has been calculated for the energy modelling. This should be based on a dynamic calculation of the system boundaries over the course of a year i.e. incorporating variations in source temperatures and the design sink temperatures (for space heat and hot water). c. The expected heat source temperature and the heat distribution system temperature with an explanation of how the difference will be minimised to ensure the system runs efficiently. The distribution loss factor should be calculated based on the above information and used for calculation purposes. The applicant should also confirm if ASHP can be used to serve all heating loads for the development which would omit the requirement for electric boilers. Furthermore, the applicant should confim if the system will be configured in such as way to recovery heat from the non-domestic element (cooling demands) to be used on the domestic element. | SCOP and SEER were determined based on project experience from manufacturer data with typical values deemed appropriate to the proposed development. Further details will be determined at the next design stage. The ASHP system is proposed to generate LTHW up to 48°C. When LTHW is required at higher temperatures that would negatively affect the ASHP SCOP (commercial calorifiers and residential heat network), electric boilers are proposed to top-up the LTHW temperature. The heating system shall not be oversized and the primary loop LTHW return temperature shall be kept low. Adequate LTHW pipework insulation to be provided to minimize distribution heat losses.
The developent is proposed to be served by a communal energy centre shared by all users (hotel, office, gym and residential). Please see heating schematic attached. Electric boilers are required to top-up the LTHW temperature serving the commercial domestic hot water calorifers and the residential heat network. The commercial areas (hotel, office and gym) space heating is proposed to be generated 100% via ASHPs. Note that the commercial domestic hot water and the residential heat network branches are proposed to be pre-heated via the 4-pipe ASHP system, therefore maximising the amount of heat that can be generated efficiently via ASHPs. In addition, the 4-pipe ASHP/chiller system is designed to recover heat from the non-domestic element (cooling demand) to be used on the domestic element, when there is simultaneus heating and cooling demand. If the entire development was to be served by ASHPs only (without electric boilers), this would reduce the efficiency of the ASHPs and the available roof space has already been maximised.
Carbon performance and offsetting
16 | The applicant has provided the relevant modellings output sheets (i.e. TER, DER, BRUKL) for the Baseline, Be Lean and Be Green stages of the energy hierarchy. | N/A
17 | The carbon dioxide savings exceed the on-site target set within the London Plan for the new build domestic and non-domestic uses. The applicant should confirm if they have included the new build element site total only within their energy statement. If this is not currently included then this must be submitted. | The Energy Statement presented the carbon emission savings for the whole development (including refurbishment) and separately the savings associated with the refurbishment only. The overall carbon emissions from the new build only will be 39.6% corresponding to 267.4 tonnes of regulated CO2 reduction saving.
18 | The applicant should confirm the associated carbon offset payment that will be made to the borough. for the shortfall of 432 tonnes annually. They should also provide draft S106 wording for the payment mechanism for the offset as they have indicated that this will not be confirmed until the detailed design stage. | With the SAP10 carbon factors, to achieve ‘zero carbon’ for the residential portion of the scheme, 36.6 tonnes per annum of regulated CO2, equivalent to 1099.3 tonnes over 30 years, from the new-build domestic portion should be offset offsite. The shortfall to a zero carbon reduction from baseline for the new build nondomestic portion of the scheme has been revised to 367.5 tonnes per annum of regulated CO2, equivalent to 11,025 tonnes over 30 years, to be offset offsite (excluding the refurbishment part of the development). Based on current tools and methodology available for calculation of CO2 emissions under SAP10 the new build part of the development will have a shortfall of 407.7 tonnes of carbon annually corresponding to circa 12,230 tonnes of CO2 over 30 years. For the GLA carbon offsetting price of 95£/tonne a total figure of circa £1,161,800 is expected to be required. These figures should be confirmed via detailed design stage calcualtions based on the adopted SAP10 metholdology at the time the section106 is due. GE to advise
Whole Life-Cycle Carbon Assessment
19 | The applicant should submit a WLC assessment which will be reviewed separately; comments will be provided. The WLC assessment should follow the GLA WLC guidance and reporting template (https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/planning-guidance/whole-life-cycle-carbon-assessments-guidance-pre-consultation-draft). Applicants will also be conditioned to submit a post-construction assessment to report on the development’s actual WLC emissions. | This was issued as part of the application, please refer to the accompanying document.
Be Seen' Energy Monitoring
20 | The applicant has provided a commitment that the development will be designed to enable post construction monitoring and that the information set out in the ‘be seen’ guidance is submitted to the GLA’s portal at the appropriate reporting stages. This will be secured through suitable legal wording. The first submission of the planning stage data should be provided to the GLA through the be seen reporting spreadsheet within four weeks of planning approval. | The Be Seen reporting spreadsheet is not yet been made available and a request for planning stage data to be submitted four weeks of planning approval seems a short timeframe for adequate completion. It is proposed that this is a pre-commence or pre-occupation condition.
Other points
25 | The applicant should complete and submit the Good Homes Alliance Early Stage Overheating Risk Tool. | Please see attached.
Move resolved comments under this section

## CO2 performance
Domestic
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations | 73.3
Energy Efficiency | 60.7 | 12.6 | 17.19%
CHP | 60.7 | 0 | 0%
Renewable energy | 40.1 | 20.6 | 28.1%
Total |  | 33.2 | 45.29%
Non-domestic
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations | 649.8
Energy Efficiency | 587.7 | 62.1 | 9.557%
CHP | 587.7 | 0 | 0%
Renewable energy | 392.1 | 195.6 | 30.1%
Total |  | 257.7 | 39.66%
Carbon offsetting
| Shortfall (tonnes per annum) | Shortfall (£)
Domestic | 1204 | 114358
Non-domestic | 11762 | 1117354
Total | 12966 | 1231712