|  | S |
| --- | --- |

ENVIRONMENTAL HEALTH

SUPPORTING COMMUNITIES

| To: | Adam Greenhalgh, Planning Officer, Development Management, 5 Pancras Square N1C |
| --- | --- |
| From: | Edward Davis (Pollution Planning Officer) |
| Date: | 15 June 2021 |
| Re: | 155 & 157 Regent's Park Road London NW1 8BB |
| Proposal: | Demolition of existing building and redevelopment to provide a part 4 storey/part 7 storey building, with two basement levels, for a 59 bedroom hotel, with new street level public realm works in front (at junction of Regent's Park Road, Adelaide Road and Haverstock Hill). |
| Reference: | Planning application ref. 2021/0877/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

The site is located at 155 - 157 Regents Park Road, London, NW1 8BB. It is bounded to the north by Adelaide Road, to the east by Haverstock Hill (A502), to the south by Regent’s Park Road and to the west by existing residential properties.

The nearest residential properties are directly adjacent to the development site, to the west, on Adelaide Road and Regent’s Park Road.

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, Camden Council’s Local Plan, version June 2017 and BS 8233:2014.

The proposed development includes noise-generating building services plant which have the potential to have an impact upon existing noise sensitive receptors in the locality of the site.

It is understood that externally mounted building services plant, located at roof top level within a plant enclosure will include:

▪ One Air handling Unit (AHU);

▪ Five VRF Condensers REYQ22T: each of it is made up of two 12T units.

It is proposed that the plant items will be operating during day and night-time periods.

Based on the results of the acoustic submission and relevant guidance, noise emission limits have been identified for proposed new items of plant and equipment. If these noise limits are complied with, it is considered unlikely that adverse noise effects will occur as a result of the proposed development and are likely to fall within theL (Lowest Observable Effect Level) threshold and therefore acceptable in environmental health terms.

A 2.5 m plant enclosure has been considered within the submitted calculations and the predicted noise level attributable to all building services plant at the nearest noise sensitive façade is 30 dB LAr,Tr. It can be seen therefore that the criteria (≤ 30 dB dB LAr,Tr) can be achieved.

Indicative façade / glazing performance guidance has been provided for the development based on internal ambient noise level guidelines from BS 8233: 2014.

Measured VDVs at the site are significantly below LBC criteria. Based on the assessment results and in light of BS 6472-1 criteria, ‘adverse comment is not expected’.

Therefore, the submitted design information is reasonable in environmental health terms and I would not be offering any objections and suggest the following should you be mindful to grant the application

Suggested Condition:

The design and structure of the development shall be of such a standard that it will protect residents within it from existing external noise so that they are not exposed to levels indoors of more than 35dB LAeq 16hrs daytime and of more than 30 dB LAeq 8hrs in bedrooms at night

Reason: To safeguard the amenities of the adjoining premises and the area generally in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017.

Prior to the commencement of development, to include demolition, a Construction Environmental Management Plan shall be submitted to and approved in writing by the Local Planning Authority. The Construction Environmental Management Plan shall identify the steps and procedures that will be implemented to minimise the creation and impact of noise, air quality*, vibration, dust** and waste disposal resulting from the site preparation, groundwork and construction phases of the development and manage Heavy Goods Vehicle (HGV) access to the site.  Measures to minimise the impact on air quality should include HGV routes avoiding Air Quality Management Areas and avoid vehicle idling. The approved Construction Environmental Management Plan shall be adhered to at all times, unless otherwise first agreed in writing with the Local Planning Authority.

* The Institute of Air Quality Management http://iaqm.co.uk/guidance/

** The applicant should have regard to BRE guide 'Control of Dust from Construction and Demolition, February 2003

Reason: To ensure that the amenities of occupiers of other premises in the vicinity are protected.

Construction noise and vibration levels should be as follows:

| Day | Time Period | Averaging Time T | *Threshold Level dB LAeq, T |
| --- | --- | --- | --- |
| Monday to Friday | 07:00 – 08:00 08:00 – 18:00 18:00 – 19:00 19:00 – 22:00 22:00 – 07:00 | 1 hr 10 hr 1 hr 3 hr 1 hr | 70 75 70 65 55 |
| Saturday | 07:00 – 08:00 08:00 – 13:00 13:00 – 14:00 14:00 – 22:00 22:00 – 07:00 | 1 hr 5 hr 1 hr 3 hr 1 hr | 70 75 70 65 55 |
| Sunday and Public Holidays | 07:00 – 21:00 21:00 – 07:00 | 1 hr 1 hr | 65 55 |

*The threshold level is the values in this column or where the total noise (construction noise plus ambient noise) is 5dB above the pre-existing baseline noise level for the corresponding time of the day, whichever is the higher. The threshold being the level at which we recognise additional noise mitigation or programming is required to address noise levels so that where practicable they are reduced to below the threshold level.

Vibration Levels:

| Place and time | Low probability of adverse comment VDV ms -1.75 (Vibration Dose Value) | Adverse comment possible VDV ms -1.75 (Vibration Dose Value) | Adverse comment probable VDV ms -1.75 (Vibration Dose Value) |
| --- | --- | --- | --- |
| Residential buildings 16 hour day | 0.2 – 0.4 | 0.4 – 0.8 | 0.8 – 1.6 |
| Residential buildings 8 hour night | 0.1 – 0.2 | 0.2 – 0.4 | 0.4 – 0.8 |

Prior to commencement of the development, details shall be submitted to and approved in writing by the Council, of an enhanced sound insulation value DnT,w of at least 5dB above the Building Regulations value, for the floor/ceiling/wall structures separating different types of rooms/ uses in adjoining dwellings, namely [eg. living room and kitchen above bedroom of separate dwelling].  Approved details shall be implemented prior to occupation of the development and thereafter be permanently retained.

Reason: To safeguard the amenities of the adjoining premises and the area generally in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017.

At least 21 days prior to the commencement of any site works, all occupiers surrounding the site should be notified in writing of the nature and duration of works to be undertaken. The name and contact details of a person responsible for the site works should be made available for enquiries and complaints for the entire duration of the works and updates of work should be provided regularly. Any complaints should be properly addressed as quickly as possible.

No waste materials should be burnt on site of the development hereby approved.

If you have any queries, please do not hesitate to contact me.

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967652382