|  | S |
| --- | --- |

ENVIRONMENTAL HEALTH

SUPPORTING COMMUNITIES

| To: | Matthew Dempsey, Planning Officer, Development Management, 5 Pancras Square N1C |
| --- | --- |
| From: | Edward Davis (Pollution Planning Officer) |
| Date: | 04 November 2021 |
| Re: | 178B Royal College Street, and Arches 73, 74 and 75 Randolph Street. London NW1 0SP |
| Proposal: | Amalgamation of 178B Royal College Street with Arches 74 and 75 and part of Arch 73 to create commercial kitchen and delivery centre with ancillary offices (sui generis). External alterations to shopfront of 178B Royal College Street and provision of plant and machinery to the rear of the Arches 73, 74 and 75. (Retrospective). |
| Reference: | Planning application ref. 2021/4163/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

The development is located under a railway line with the entrance on Royal College Street and Randolph Street. The extraction system is located on the North wall of the premises with the flue running along the railway.

It in envisaged that the development will operated between 08:00 -23:00.

A noise assessment has been submitted which evaluates the potential noise impact of the proposed installation at the closest and most affected existing residential receptors.

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, Camden Council’s Local Plan, version June 2017 and BS 4142:2014.

The nearest sensitive receptor has been identified as the first floor dwelling west of the extraction exhaust

The noise level measured approx. 1m from the sensitive receptor was calculated to be 46.5dB which is 3.4dB above the background level and non-compliant to current guidance.

The applicant has received designs of attenuators that should reduce the noise level by at least 13.4dB

I am satisfied that the submitted acoustic submission should meet our local plan guidelines with the proposed mitigation and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application. It must be noted that a further assessment is advisable to ensure the new mitigation measures are in compliance.

Additionally, as there are new components to be added to the system that may affect the odour abatement of the system it is also essential the applicant ensures the odour system is not compromised by the alteration. This can be dealt with by way of appropriate conditioning.

Suggested conditions:

Prior to use of the development, details shall be submitted to and approved in writing by the Council, of the external noise level emitted from plant/ machinery/ equipment and mitigation measures as appropriate.  The measures shall ensure that the external noise level emitted from plant, machinery/ equipment will be lower than the lowest existing background noise level by at least 10dBA, by 15dBA where the source is tonal, as assessed according to BS4142:2014 at the nearest and/or most affected noise sensitive premises, with all machinery operating together at maximum capacity. A post installation noise assessment shall be carried out where required to confirm compliance with the noise criteria and additional steps to mitigate noise shall be taken, as necessary.  Approved details shall be implemented prior to occupation of the development and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to commencement of the development, details of anti-vibration measures shall be submitted to and approved in writing by the Council.  The measures shall ensure that the extract/ ventilation system and ducting are mounted with proprietary anti-vibration isolators and fan motors are vibration isolated from the casing and adequately silenced.  Approved details shall be implemented prior to occupation of the development and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to commencement of the use, details shall be  submitted to and approved in writing by the Council, of the installation, operation, and maintenance of the odour abatement equipment and extract system, including the height of the extract duct and vertical discharge outlet, in accordance with the ‘Guidance on the assessment of odour for planning 2018 by the Institute of Air Quality Management .  Approved details shall be implemented prior to the commencement of the use and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by cooking odour

If you have any queries, please do not hesitate to contact me.

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967652382