|  | S |
| --- | --- |

ENVIRONMENTAL HEALTH

SUPPORTING COMMUNITIES

| To: | Matthew Dempsey, Planning Officer, Development Management, 5 Pancras Square N1C |
| --- | --- |
| From: | Edward Davis (Pollution Planning Officer) |
| Date: | 22 November 2021 |
| Re: | 112A Camden Road London NW1 9EE |
| Proposal: | Alterations to shop front and installation of extraction vent to rear related to change in operation form vacant shop (A1) to restaurant (A3). |
| Reference: | Planning application ref. 2021/4964/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

The application site is located on the east side of Camden Road..

I have reviewed the submitted acoustic information by ‘Aval Consulting’ and ventilation design information.

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, Camden Council’s Local Plan, version June 2017 and BS 4142:2014.

The calculations show that the noise emission levels of the proposed plant strategy meet the Local Authority criteria during the operating period with additional mitigation and should not have an adverse impact on the nearest sensitive receivers. Odour design has also been adequately considered in the design submission.

I am satisfied that the submitted acoustic submission and odour details meets our local plan guidelines and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

The external noise level emitted from plant, machinery or equipment at the development hereby approved shall be lower than the lowest existing background noise level by at least 10dBA, by 15dBA where the source is tonal, as assessed according to BS4142:2014 at the nearest and/or most affected noise sensitive premises, with the machinery operating at maximum capacity.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

The installation, operation, and maintenance of the odour abatement equipment and extract system, including the height of the extract duct and vertical discharge outlet shall be in accordance with the ‘Guidance on the assessment of odour for planning 2018 by the Institute of Air Quality Management.  Approved details shall be implemented prior to the commencement of the use and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by cooking odour

If you have any queries, please do not hesitate to contact me.

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967652382