|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Josh Lawlor, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 02 December 2021 |
| Re: | 5 Elm Row London NW3 1AA v1 |
| Proposal: | Alterations to one external window. Installation of two air source heat pumps to roof |
| Reference: | Planning application ref. 2021/4513/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

I have reviewed the submitted acoustic assessment by ‘Clements Acoustics, dated December 2021, document ref: 17263-NIA-01.

Appropriate noise guidelines have not been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), BS 4142:2014, Planning Practice Guidance on Noise, especially the Camden Council’s Local Plan, version June 2017 which sets out a more robust criteria for noise from mechanical plant.

The plant noise levels have been adequately predicted at the at the identified receptors taking into consideration distance losses, surface acoustic reflections and, where applicable any screening provided by the building.

Based on the results of the submitted noise assessemnet, noise limits for the new plant have been adequately calculated.

The calculations show that the noise emission levels of the proposed plant strategy meet the Local Authority criteria during the operating period with specified mitigation and should not have an adverse impact on the nearest sensitive receivers.

I am satisfied that the submitted acoustic submission meets our local plan guidelines given appropriate performance of the acoustic enclosure and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

As the installation is dependant of the performance of specified mitigation, prior to use of the development, details shall be submitted to and approved in writing by the Council, of the external noise level emitted from plant/ machinery/ equipment and mitigation measures as appropriate.  The measures shall ensure that the external noise level emitted from plant, machinery/ equipment will be lower than the lowest existing background noise level by at least 10dBA, by 15dBA where the source is tonal,  as assessed according to BS4142:1997 at the nearest and/or most affected noise sensitive premises, with all machinery operating together at maximum capacity. Approved details shall be implemented prior to occupation of the development and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

If you have any queries, please do not hesitate to contact me.

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967 652382