|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | David Fowler, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 27 January 2022 |
| Re: | Royal Free Hospital Pond Street London NW3 2QG |
| Proposal: | Installation of 2 x Chillers and associated plant enclosure on the 4th floor podium roof facing north as a small increase to a planning permission for the initial chillers and plant room 2019/5370/P dated 24/01/20. |
| Reference: | Planning application ref. 2021/4596/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

The site is located on Pond Street in the Hampstead District in North West London.

The area consists of a mixture of residential and commercial premises with the sound sensitive façades being identified as the residential premises in Pond Street. The sound sensitive facade has partial direct line of site to the plant with some screening from the building edge.

It is understood the gym will operate 24 hours a day, seven days a week. Building services plant may be running at any time during such periods.

12 number – Mitsubishi EACV-P900YA-N Air Cooled Chiller units are being proposed for the site.

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, Camden Council’s Local Plan, version June 2017 and BS 4142:2014.

The plant noise levels have been adequately predicted at the at the identified receptors taking into consideration distance losses, surface acoustic reflections and, where applicable, screening provided by the building.

Based on the results of the submitted noise assessemnet, noise limits for the new plant have been adequately calculated.

The calculations show that the noise emission levels of the proposed plant strategy meet the Local Authority criteria during the operating period and should not have an adverse impact on the nearest sensitive receivers.

I am satisfied that the submitted acoustic submission meets our local plan guidelines given appropriate performance of the acoustic installation and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

The external noise level emitted from plant, machinery or equipment at the development hereby approved shall be lower than the lowest existing background noise level by at least 10dBA, by 15dBA where the source is tonal, as assessed according to BS4142:1997 at the nearest and/or most affected noise sensitive premises, with all machinery operating together at maximum capacity.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

If you have any queries, please do not hesitate to contact me.

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967 652382