## Case details
Energy Memo: GLA Consultation
Case details
Date of first review: | 2022-01-27
Case Name: | Murphy's Yard, Kentish Town NW5
Case Number: | 2022/0003
Case Officer: | Andrew Payne
London Borough: | Camden
Application Type (Outline/Hybrid/Detailed): | Outline
Applicant: | Folgate Estates Ltd
Energy Consultant: | Hoare Lea
Document Title: | Energy Strategy
Document Date: | 2021-06-01
Development proposals
Use | Floorspace/Number of units
Residential | 750-825 units
Residential institution floorspace (Use Class C2) | up to 8,0000 m²
Industrial floorspace within Use Classes E(g)(iii), B2 and B8 | minimum of 40,461 m²
General industrial and/or storage floorspace [Use Class B2 and/or B8] | up to 8,150 m²
Light industrial floorspace (Class E(g)(iii)) | up to 36,043 m²
Office floorspace | up to 34,500 m²
research and development floorspace (Class E(g)(ii)) | up to 36,000 m²
Healthcare floorspace (Class E(e)) | up to 16,000 m²
Flexible commercial and sui generis floorspace (Use Class E and/or Sui Generis Use) | 1,300-3,650 m²
Community floorspace (F1 and/or F2) | 300-1,300 m²
Flexible mixed-use space (Class Sui Generis) | up to 1,500 m²

## Energy Comments
Compliance Schedule - To be completed by the GLA Energy Officer
| Policy | Policy Sub-Area | Required Data (In line with EAG) | Status | Policy Compliance | GLA Comment Reference
| SI 1 - Improving Air Quality (relating only to air quality impacts of energy systems; separate air quality officer consultation required) | Measures/design features to reduce exposure to air pollution | Measures to minimise NOx emissions from energy systems | N/A | Compliant
| SI 2 - Minimising Greenhouse Gas Emissions (excluding SI-2-F- WLC; separate WLC consultation required) | Be Lean emissions reduction | Details of energy efficiency measures | Received but items still outstanding | Potential Compliance-Pending Information
|  |  | Alignment with Cooling and Overheating | Received but items still outstanding |  | Detailed comment 6
|  |  | Be Lean 10% and/or 15% reduction achieved | Received but items still outstanding |  | Detailed comment 3,4
|  | Renewable generation maximisation | Roof Layout detailing PV proposal | Not yet received - applicant to submit and provide reference --->
|  |  | PV array metrics provided | Not yet received - applicant to submit and provide reference --->
|  |  | Heat Pump arrangement confirmed | Not yet received - applicant to submit and provide reference --->
|  | Total carbon reduction on-site | Confirmation of carbon emission factors used | Received; SAP 10 proposed and nothing further required
|  |  | GLA carbon emission reporting spreadsheet v1.2 | Not yet received - applicant to submit and provide reference --->
|  |  | Supporting Modelling Ouputs (BRUKLs/DER Worksheets) | N/A
|  | Carbon offset payment confirmed | Draft S106 wording of carbon offset (from borough) | Not yet received - applicant to submit and provide reference --->
|  | Be Seen commitment provided | Written confirmation/understanding of data requirements | Received and nothing further required
|  |  | Confirmation of Planning Stage 1 submission | Not yet received - applicant to submit and provide reference --->
| SI 3 - Energy Infrastructure | Engagement with DHN Stakeholders | Applicant/Stakeholder Correspondence | Not yet received - applicant to submit and provide reference ---> | Potential Compliance-Pending Information
|  | Aligned with heating hierarchy | Heating system details provided | Received but items still outstanding |  | Detailed comment 8,9,11
|  | Acceptable Design | Futureproofed DHN connection drawings | N/A
|  |  | Site heat network drawings | N/A
|  |  | Details of management measures proposed | Not yet received - applicant to submit and provide reference --->
| SI 4 - Managing Heat Risk | Aligned with cooling hierarchy | Completed GHA overheating tool | Received but items still outstanding | Potential Compliance-Pending Information | Detailed comment 6
|  | Compliance with GLA Cooling Metrics | CIBSE dynamic overheating analysis | N/A
|  |  | Confirmation that cooling criteria have been met | Received but items still outstanding |  | Detailed comment 6,7
| Application Metrics | Stage 1 Value | Final Value
| Domestic carbon emissions | TBC
| Non-domestic carbon emissions | TBC
| Carbon offset payment amount | TBC
| kWp renewable generation capacity | TBC
| kWh annual renewable energy generation | TBC
| Sqm of proposed PV array | TBC
| Calculated SCOP of heat pumps | TBC
| Heat fraction provided by heat pumps | TBC
| Flow/Return temperatures proposed | N/A
| Distribution loss assumption | N/A
| Whole Life Carbon Assessment | Received and Under Separate Consultation
Innovative Features
Detailed Comments - Applicant MUST provide detailed responses to the below items
Comment No. | GLA Stage I | Applicant's Stage I response | GLA Post Stage I response | Applicant's Post Stage I response
| Date: 27/01/2022 | Date: 22.02.22 | Date: | Date:
Documents to be secured
Energy Strategy 01/06/2021
General compliance comments
1 | The energy strategy is generally compliant with the London Plan 2021 policies however, the applicant is required to submit the additional information, which has been requested below. The applicant's response to GLA's energy comments should be provided directly within this Energy Memo. Any wider supporting material submitted should be referenced within the applicant's memo response. | Noted
2 | The applicant should submit the GLA’s Carbon Emission Reporting spreadsheet in excel format; this has been developed to allow the use of the updated SAP 10 emission factors alongside the SAP 2012 emission factors. [The link to the spreadsheet can be found here: https://www.london.gov.uk/what-we-do/planning/planning-applications-and-decisions/pre-planning-application-meeting-service-0] | As this is an outline application and we have no detailed drawings to model, we do not have any calculations with which to poppulate into this spreadsheet
Be Lean
3 | The applicant should provide some representative modelling to indicate the expected performance of the domestic element of the development and the estimated CO2 emissions at this stage. They will be required to provide detailed modelling as part of a future reserved matters applications. The applicant should be conditioned for reserved matters applications to demonstrate a minimum 10% domestic Be Lean reduction in regulated CO2 emissions compared to a 2013 Building Regulations compliant development and to submit detailed energy modelling outputs (DER/TER Worksheets). | Noted
4 | The applicant should provide some representative modelling to indicate the expected performance of the non-domestic element of the development and the estimated CO2 emissions at this stage. They will be required to provide detailed modelling as part of a future reserved matters applications. The applicant should be conditioned for reserved matters applications to demonstrate a minimum 15% non-domestic Be Lean reduction in regulated CO2 emissions compared to a 2013 Building Regulations compliant development and to submit detailed energy modelling outputs (BRUKL Worksheets. | Noted
5 | The applicant should consider and minimise the estimated energy costs to occupants and outline how they are committed to protecting the consumer from high prices. This should cover the parameters set out in the guidance and include a confirmation of the quality assurance mechanisms that will be considered as part of the strategy. The applicant should be conditioned for reserved matters applications to submit information to demonstrate they have considered and minimised the estimated energy costs to occupants and outline how they are committed to protecting the consumer from high prices. This should cover the parameters set out in the guidance and include a confirmation of the quality assurance mechanisms that will be considered as part of the strategy. | Noted
Overheating
6 | The applicant has submitted the Good Homes Alliance Early Stage Overheating Risk Tool. They should seek to introduce where possible further "key factors reducing the likelihood of overheating". Commentary should be provided regarding the opportunities and constraints for this. They have also outlined measures in response to the cooling hierarchy. They propose low g-values, recessed external windows, natural and mechanical ventilation. The applicant has also stated that although comfort cooling does not form part of the current strategy to the residential units, passive cooling will be provided through the MVHR Units – in the form of a tempered air supply. The applicant should first follow the cooling hierarchy and then if needed suggest active cooling if needed. Active cooling if utilised, should be minimised. They should be conditioned to undertake as part of the reserved matters application a Dynamic Overheating Analysis to assess the overheating risk. This should follow the CIBSE TM59 methodology for the London Design Summer Year 1 (DSY1) weather file: 2020s, High emission, 50% percentile scenario. The applicant should also investigate the risk of overheating using the DSY 2 & 3 weather files. | Noted
7 | The applicant has provided a commitment that the actual building’s cooling demand will be lower than the notional. The applicant should be conditioned to demonstrate as part of the reserved matters applications that any active cooling provision is lower than the notional in (MJ/m2). They should be conditioned to undertake as part of the reserved matters application a Dynamic Overheating Analysis to assess the overheating risk for any naturally ventilated non-domestic spaces. This should follow the CIBSE TM52 methodology for the London Design Summer Year 1 (DSY1) weather file: 2020s, High emission, 50% percentile scenario. The applicant should also investigate the risk of overheating using the DSY 2 & 3 weather files. | Noted
Be Clean
8 | The applicant has carried out an investigation and there are no existing or planned district heating networks within the vicinity of the proposed development. They should contact relevant stakeholders including the borough energy officer, local heat network operators and nearby developers and ask whether they know of any local heat network connection opportunities. Evidence of the correspondence should be submitted. Due to the large scale of the scheme, they should also explore the potential to catalyse the creation of a wider network and export heat. Evidence of correspondence with relevant stakeholders (including the borough) on this point should be submitted. Due to the different uses within the site the applicant should explore the potential for large scale heat recovery on site. | No response was received from Camden during the pre-planning stage. A further request has been made. We will investigate opportunities to export heat and look at recovery
9 | The applicant is proposing a site-wide heat network supplied by a centralised energy centre. It should be confirmed that all apartments and non-domestic building uses will be connected to the heat network. The applicant has provided a commitment that the development is designed to allow future connection to a district heating network. This should include a single point of connection to the district heating network. The applicant should be conditioned to demonstrate, as part of the reserved matters applications, detail confirming the development is designed to allow future connection to a district heating network. | All building uses (domestic and non-domestic) will be connected to the site wide heat network. The future proofed connection to a DHN will be a single point of connection
Be Green
10 | The applicant has confirmed that PV panels will be proposed. An estimation of the amount should be provided. An indicative detailed roof layout should be provided demonstrating that the roof’s potential for a PV installation has been maximised and clearly outlining any constraints to the provision of further PV, such as plant space or solar insolation levels. The applicant is expected to situate PV on any green/brown roof areas using biosolar arrangement and should indicate how PV can be integrated with any amenity areas. The on-site savings from renewable energy technologies should be maximised regardless of the London Plan targets having been met. The applicant should provide the capacity (kWp), total net area (m2) and annual output (kWh) of the proposed PV array. The applicant should be conditioned to submit, as part of the reserved matters applications, a detailed roof layout demonstrating that the roof’s potential for a PV installation has been maximised and clearly outlining any constraints to the provision of further PV, such as plant space or solar insolation levels. The applicant is expected to situate PV on any green/brown roof areas using biosolar arrangement and should indicate how PV can be integrated with any amenity areas. The on-site savings from renewable energy technologies should be maximised regardless of the London Plan targets having been met. | Noted
11 | Heat pumps are being proposed in the form of a (centralised) ASHP. ASHP technology would be utilised to provide space heating, cooling and a proportion of the domestic hot water demand. the remaining DHW demand will be met via electric instantaneous units and electric instantaneous units. The indicative heat pumps percentage of contribution to the site’s heat loads should be provided together with an indicative COP. At the reserved matters stage, the applicant should be conditioned to provide full details of the ASHP proposals including: a. An estimate of the heating and/or cooling energy (MWh/annum) the heat pumps would provide to the development and the percentage of contribution to the site’s heat loads. They should demonstrate how the heat fraction from heat pump technologies has been maximised. b. Details of the Seasonal Coefficient of Performance (SCOP) and/or Seasonal Energy Efficiency ratio (SEER) and how these have been calculated. This should incorporate the expected heat source and heat distribution temperatures (for space heat and hot water)and the distribution loss factor, which should be calculated based on the above information and used for calculation purposes. | Noted
Whole Life-Cycle Carbon Assessment
12 | The applicant has submitted a WLC assessment which will be reviewed separately; comments will be provided. The WLC assessment should be presented separately in excel using the GLA's WLC assessment template and should follow the GLA WLC guidance. The template and guidance are available here: https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/london-plan-guidance/whole-life-cycle-carbon-assessments-guidance. Applicants will also be conditioned to submit a post-construction assessment to report on the development’s actual WLC emissions. | This has been responded to seperately
Be Seen Energy Monitoring
13 | The applicant should review the ‘Be Seen’ energy monitoring guidance to ensure that they are fully aware of the relevant requirements to comply with the ‘Be Seen’ policy. The guidance is available here: https://consult.london.gov.uk/be-seen-energy-monitoring. A commitment has been provided that the development will be designed to enable post construction monitoring and that the information set out in the ‘Be Seen’ guidance is submitted to the GLA’s portal at the appropriate reporting stages. This will be secured through suitable legal wording. The first submission of the planning stage data should be provided to the GLA through the be seen planning stage webform (https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/london-plan-guidance-and-spgs/be-seen-energy-monitoring-guidance) at the planning submission stage, alongside the energy statement. The 'Be Seen' reporting spreadsheet has been developed to enable development teams to capture all data offline before this is submitted via the webform. The applicant should confirm that the planning stage data has been submitted to GLA. | Noted
Other points
14 | The applicant should confirm the carbon shortfall in tonnes CO2 and the associated carbon offset payment that will be made to the borough. This should be calculated based on a net-zero carbon target for domestic and non-domestic proposals using the GLA’s recommended carbon offset price (£95/tonne) or, where a local price has been set, the borough’s carbon offset price. The draft s106 agreement should be submitted when available to evidence the agreement with the borough. | Noted
15 | The applicant should be conditioned to submit the energy statements in the reserved matters application for review and approval by the borough and GLA, and to address the other items referenced above. | Noted
Move resolved comments under this section
Received; SAP 10 proposed and nothing further required
Received; SAP 2012 proposed and nothing further required
Received; SAP 10 proposed but items still outstanding
Received; SAP 2012 proposed but items still outstanding
Not yet received - applicant to submit and provide reference --->
N/A

## CO2 performance
Domestic
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations | TBC
Energy Efficiency | TBC | #VALUE! | #VALUE!
CHP | TBC | #VALUE! | #VALUE!
Renewable energy | TBC | #VALUE! | #VALUE!
Total |  | #VALUE! | #VALUE!
Non-domestic
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations | TBC
Energy Efficiency | TBC | #VALUE! | #VALUE!
CHP | TBC | #VALUE! | #VALUE!
Renewable energy | TBC | #VALUE! | #VALUE!
Total |  | #VALUE! | #VALUE!
Carbon offsetting
| Shortfall (tonnes per annum) | Shortfall (£)
Domestic | TBC | #VALUE!
Non-domestic | TBC | #VALUE!
Total | 0 | #VALUE!