## Sheet1
Disinfection of Service Pipes and Private Mains
Company Name | OLW CConstruction Ltd
Name | Mark Aldous
Date | 2022-09-09
Site Address | 1 Hampshire Street, Kentish Town, NW5 2TE
Pipe -Length,size, | 63mm Barrier pipe, 8meters
type
Pre- Disinfection
Flush Time |  |  |  |  | 30 | Mins
Pre- Disinfection Chlorine Levels of Incoming Water |  |  |  |  | 0.17 | mg/l
Disinfection
Initial Chlorine Level |  |  |  |  | 0.5 | mg/l
Contact Time |  |  |  |  | 1200 | Mins
Chlorine level after contact time |  |  |  |  | 0.48 | mg/l
Sodium Hypochlorite |  |  |  |  | Yes
Post Disinfection
Chlorine Level after flushing |  |  |  |  | 0.5 | mg/l
Time/date labortary samples taken |  |  |  |  | 08 30am | Time
[5 empty] | 2022-02-04 | Date
Declaration
I confirm that this disinfection has been carried out in accordance with |  |  |  | Mark Aldous
BS EN 806 and that thepipe has been left sealed awaiting connection.
Bacteriological Testing
Test |  |  | Results
Free Chlorine |  |  | Less than 0.01 mg/l
Total Chlorine |  |  | 0.12
Total Coliforms per 100ml |  |  | 0 mpn / 100ml
Total E.Coli per 100ml |  |  | 0 mpn / 100ml
Turbidity |  |  | Less than 1 FTU
pH
Taste and Odour |  |  | Clear