|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Matthew Dempsey, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 19 July 2022 |
| Re: | 230 Camden High Street London NW1 8QS |
| Proposal: | Installation of kitchen extraction system and external ducting at rear elevation of ground floor flat roof; and, providing 3 air condition units at rear elevation wall including relocation of existing rear access. |
| Reference: | Planning application ref. 2022/1028/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

The development site building is bounded by ’Evil from the Needle’ tattoo shop to the North, office buildings to the West, People’s fish and chip shop to the South and Camden High Street to the East

The proposals are to install 1No. MUB 042 500D4 IE2 Multibox Extraction Fan

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, Camden Council’s Local Plan, version June 2017 and BS 4142:2014.

The closest noise sensitive receptor to the proposed installation location has been identified as being office building windows facing the rear façade of 230 Camden High Street.

I have noted that the proposed kitchen extract fan unit is to be installed within the ground floor kitchen and therefore located out of line of site of the sensitive receptor window due to screening from the building envelope.

The plant noise criteria have been adequately predicted.

In order to control the nise emissions from the kitchen xtraction system duct termination point, an acoustic silencer is being proposed to be installed.

Mitigation may be required to meet the proposed plant noise criteria, this may take the form of a louvered enclosure. Plant should also be fitted with suitable vibration isolators, to prevent additional noise be caused through vibration.

Based on the results of the submitted noise assessemnet, the noise criteria for the new plant have been adequately calculated.

Calculations for the proposed plant strategy cannot be assessed as there has been no plant specification made and a further assessment will need to be carriedout to show compliance to the proosed noise criteria.

The submitted odour management assessment meets current guidelines and therefore acceptable in environmental health terms.

I am satisfied that the submitted acoustic submission calculates a noise criteria to be met that will meet our local plan guidelines and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

The external noise level emitted from plant, machinery or equipment at the development hereby approved shall be lower than the lowest existing background noise level by at least 10dBA, by 15dBA where the source is tonal, as assessed according to BS4142:1997 at the nearest and/or most affected noise sensitive premises, with all machinery operating together at maximum capacity. Approved details shall be implemented prior to occupation of the development and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

The installation, operation, and maintenance of the odour abatement equipment and extract system, including the height of the extract duct and vertical discharge outlet, shall be in accordance with the ‘Guidance on the assessment of odour for planning 2018 by the Institute of Air Quality Management .  Approved details shall be implemented prior to the commencement of the use and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by cooking odour

If you have any queries, please do not hesitate to contact me.

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967 652382