## Sheet1
BRILL PLACE PLANT SCHEDULE
REF. NO. | LOCATION | MODEL | QUANTITY |  | REFRIGERENT | AMBIENT TEMPERATURE |  | COOLING CAPACITY (EACH) | EVAPORATOR |  |  |  | CONDENSER (20% GLYCOL) |  |  |  | SOUND PRESSURE LEVEL @ 1M | OPERATING WEIGHT | ELECTRICAL |  | REMARKS
[9 empty] | CHW TEMP |  | CHW FLOW | MAX. PRESSURE DROP | CW TEMP |  | CHW FLOW | MAX. PRESSURE DROP |  |  | UNIT POWER INPUT | POWER SUPPLY
|  |  | DUTY | S/BY |  | DB °C | WB °C | kW | IN °C | OUT °C | l/s | kPa | IN °C | OUT °C | l/s | kPa | dB (A) | KG | kW | (V/Ph/Hz)
WCC-01 / 02 | BASEMENT | 30WI 1000 | 1 | 1 | HFC R-410A | 28 | 20 | 282 | 13 | 7 | 11.2 | 21.4 | 42 | 47 | 18.2 | 44.2 | 71.8 | 1378 | 88 | 400/3/50 | SIZE - 2099(L) X 966(W) X 1869 (H)
SR. NO. | REF.NO. | LOCATION | SYSTEM | MAKE & MODEL | MEDIUM | QUANTITY | QTY |  | CAPACITY EACH | FLOW | ENTERING WATER TEMP | LEAVING WATER TEMP | ADIABATIC SPRAY SYSTEM MAX TEMP. | ADIABATIC SPRAY SYSTEM MIN PRESSURE REQ. | ADIABATIC SPRAY SWITCH POINT TEMP. | MAX. WATER CONSUMPTION | NUMBER OF FANS | TYPE OF FAN DRIVE | TOTAL FAN AIR FLOW | EACH FAN POWER | TOTAL FAN POWER | POWER SUPPLY | REMARK
[7 empty] | DUTY | S BY | (kW) | L/s | (°C) | (°C) | (°C) | BAR | (°C) | L/s |  |  | L/s | (kW) | (kW) | (V/Ph/Hz)
1 | DAC - 01 | 17TH FLOOR | ADIABATIC COOLING | GUNTNER S-GFD 090.4D/5-SD1C/2P.E | Ethylene Glycol 20% | 1 | 1 | - | 400 | 19.78 | 47 | 42 | 35 | 2 | 26.1 | 0.094 | 5 | AXIAL EC FANS | 19581 | 0.47 | 2.35 | 230/1/50 | SIZE - 6429 (W) X 1330 (D) X 2850 (H)
REF NO. | LOCATION | SERVING | SYSTEM | PUMP |  |  |  |  | ELECTRICAL |  |  |  |  | REMARKS
|  |  |  | SUPPLIER/TYPE | QTY (Nos.) |  | CAPACITY Kg/s | HEAD (kPa) | RATED POWER kW | DETAILS V / PH / HZ | STARTER | DUTIES @ RPM | SOURCE
P04 / P06 | BASEMENT | CONDENSER SYSTEM | CW | Armstrong - Vertical Inline Pump | 1 R | 1 S | 11 | 220 | 4 | 380 / 3 / 50 | VFD | 3240 | NORMAL | (1 RUN + 1 STAND BY)
P05 | BASEMENT | CONDENSER SYSTEM | CW | Armstrong - Vertical Inline Pump | 1A | - | 11 | 220 | 4 | 380 / 3 / 50 | VFD | 3240 | NORMAL | 1 ASSIST
P07 / P09 | BASEMENT | CHILLED WATER PRIMARY PUMP | CHW | Grundfos - Vertical Inline Pump | 1 R | 1 S | 6.16 | 60 | 0.75 | 380 / 3 / 50 | VFD | 3219 | NORMAL | (1 RUN + 1 STAND BY)
P08 | BASEMENT | CHILLED WATER PRIMARY PUMP | CHW | Grundfos - Vertical Inline Pump | 1A | - | 6.16 | 60 | 0.75 | 380 / 3 / 50 | VFD | 3219 | NORMAL | 1 ASSIST
P10 / P11 | BASEMENT | CHILLED WATER SECONDARY PUMP | CHW | Grundfos - Vertical Inline Pump | 1 R | 1 S | 12.485 | 247 | 7.5 | 380 / 3 / 50 | VFD | 2491 | NORMAL | (1 RUN + 1 STAND BY)
REF NO. | LOCATION | SYSTEM | MAKE | MODEL | PUMP |  |  |  |  | ELECTRICAL |  |  |  |  | REMARKS
[5 empty] | TYPE | QTY (Nos.) |  | CAPACITY Kg/s | HEAD (kPa) | RATED POWER kW | DETAILS V / PH / HZ | STARTER | DUTIES @ RPM | SOURCE
P01 / P02 | BASEMENT | LTHW | GRUNDFOS | TPE2 40-240 N-A-F-A-BQQE-HDC | Vertical Inline Pump | 1 R | 1 S | 3.685 | 150 | 1.5 | 415/3/50 | VFD | 5500 | NORMAL | (1 RUN + 1 STAND BY)
P03 | BASEMENT | LTHW | GRUNDFOS | TPE3 32-120 S-A-F-A-BQBE-CDB | Vertical Inline Pump | 1 | - | 2 | 60 | 0.25 | 415/3/50 | VFD | 3600 | NORMAL | Jockey Pump
SR.NO. | REF. NO. | LOCATION | SYSTEM | CONTROL VESSEL SIZE |  |  |  | PRESSURIZATION SKID SIZE |  |  | MAKE UP WATER PUMPS |  |  |  |  | REMARK
[8 empty] | W | D | HT ) | MODEL | FLOW | POWER | QTY | V / PH / Hz
|  |  |  | (Ltrs) | Model | DIA (MM) | HT(MM) | (m) | (m) | (m) |  | L/S | (w) | (Nos)
1 | PU01 | BASEMENT | LTHW | 600 | FLAMCO FG 600 | 790 | 1737 | 666 | 886 | 1095 | D80 | 0.1 | 3 | 1 | 230/3/50 | Top Up Pump set - 2X2.6A (230/1/50)
2 | PU02 | BASEMENT | CHW | 600 | FLAMCO FG 600 | 790 | 1737 | 666 | 886 | 1095 | D80 | 0.1 | 3 | 1 | 230/3/50 | Top Up Pump set - 2X2.6A (230/1/50)
3 | PU03 | BASEMENT | CW | 600 | FLAMCO FG 600 | 790 | 1737 | 666 | 886 | 1095 | D80 | 0.1 | 3 | 1 | 230/3/50 | Top Up Pump set - 2X2.6A (230/1/50)
REF. NO. | SYSTEM | DESCRIPTION | MODEL | VOLUME | DESIGN FLOW RATE | FILTRATION RATING | SYSTEM CONNECTION (DN) | NOMINAL PRESSURE | ELECTRICAL |  | REMARKS
[9 empty] | UNIT POWER INPUT | POWER SUPPLY
[9 empty] | kW | (V/Ph/Hz)
DA 01 | LTHW | Magnetic Air Dirt Separator | SPIROTECH SPIROCOMBI MAGNET | 5 L | 20 m3 /hr | - | 65 mm | Test Pressure 7 Bar | - | - | SIZE - (LF x D x H - 260 x 159 x 712)
DG 01 | LTHW | Degasser | Flamco Vacumat Eco 900 | - | - | - | - | PN10 | 0.75 | 1 / 230 / 50 | SIZE - (A x B x C x D - 260 x 1030 x 670 x 100)
DP 01 | LTHW | Dosing Pot | Flamco Dosing Pot 15 L | 15 L | - | - | 3/4˝ F BSP | 16 BAR | - | - | SIZE - (A x B x C x D - 1120 x 215 x 455 x 200)
SS 01 | LTHW | Filtration System | Goodwater GLF 25 p | - | 7 L/S | 50 MICRON | 11/4˝ BSPF |  | 0.075 | 1 / 230 / 50 | SIZE - (L x W x H - 850 x 435 x 955)
REF. NO. | SYSTEM | DESCRIPTION | MODEL | VOLUME | DESIGN FLOW RATE | FILTRATION RATING | SYSTEM CONNECTION (DN) | NOMINAL PRESSURE | ELECTRICAL |  | REMARKS
[9 empty] | UNIT POWER INPUT | POWER SUPPLY
[9 empty] | kW | (V/Ph/Hz)
DA 02 | Condenser System | Magnetic Air Dirt Separator | SPIROTECH SPIROCOMBI MAGNET | 13 L | 47 m3 /hr | - | 100 mm | Test Pressure 7 Bar | - | - | SIZE - (LF x D x H - 370 x 219 x 858)
DG 02 |  | Degasser | Flamco Vacumat Eco 900 | - | - | - | - | PN10 | 0.75 | 230 / 1 / 50 | SIZE - (A x B x C x D - 260 x 1030 x 670 x 100)
DP 02 |  | Dosing Pot | Flamco Dosing Pot 15 L | 15 L | - | - | 3/4˝ F BSP | 16 BAR | - | - | SIZE - (A x B x C x D - 1120 x 215 x 455 x 200)
SS 03 |  | Filtration System | Goodwater GLF 25 p | - | 7 L/S | 50 MICRON | 11/4˝ BSPF |  | 0.075 | 230 / 1 / 50 | SIZE - (L x W x H - 850 x 435 x 955)
REF NO. | LOCATION | SERVING | SYSTEM | SKID |  | PUMP |  |  | PRESSURE TANK CAPACITY (Ltr) | CISTERN CAPACITY (Ltr) | ELECTRICAL |  |  | REMARKS
|  |  |  | TYPE | SET SIZE | QTY (Nos.) | CAPACITY (l/s) | HEAD (Bar) |  |  | RATED POWER (Kw) | V / PH / HZ | SOURCE
WBT 01 | Basement | PH Plantroom | PH | Arrow Valve - "Boost A Break" 5-10A model | 650 (W) x 490 (D) x 1550 (H) | 2 (Duty Assist) | 0.4 | 4 | 24 | 100 | 4.4 | 400 / 3 / 50 | Normal | Inlet Size - DN40
REF NO. | LOCATION | SERVING | SYSTEM | SKID |  | PUMP |  |  | PRESSURE TANK CAPACITY (Ltr) | CISTERN CAPACITY (Ltr) | ELECTRICAL |  |  | REMARKS
|  |  |  | TYPE | SET SIZE | QTY (Nos.) | CAPACITY (l/s) | HEAD (Bar) |  |  | RATED POWER (Kw) | V / PH / HZ | SOURCE
WBT 02 | 17th Floor | DRY Cooler | PH | Arrow Valve - "Boost A Break" 5-16A model | 650 (W) x 490 (D) x 1550 (H) | 2 (Duty Assist) | 0.6 | 6 | 24 | 100 | 6 | 400 / 3 / 50 | Normal | Inlet Size - DN40
REF | LOCATION | DESCRIPTION | MODEL | DESIGN FLOW RATE | RESIN VOLUME | REGENERATION WASTEWATER FLOW | SYSTEM CONNECTION (DN) | DRAIN CAPACITY | SALT USED PER REGENERATION | WATER REFILL CAPACITY PER REGENERATION | ELECTRICAL |  | REMARKS
[11 empty] | UNIT POWER INPUT | POWER SUPPLY
[11 empty] | kW | (V/Ph/Hz)
WS 01 | 17TH FLOOR | Goodwater Water Softner | Pegasus 15 / 9000 | 0.2 L/S | 15 L | 0.11 L/S | 1˝ BSPF | 0.12 L/S | 2.1 KG | 6.6 L | 0.06 | 220 / 1 / 50 | SIZE - (A x B x C - 1340 x 1100 x 780)
REF | LOCATION | DESCRIPTION | MATERIAL | NOMINAL CAPACITY | ACTUAL CAPACITY | TANK SIZE | INLET CONNECTION | OVERFLOW CONNECTION | OUTLET CONNECTION | DRAIN CONNECTION | REMARKS
CWT 01 | Basement | Portable water Tank - Divided in 2 Equal halves | GRP Sectional, Pre Insulated | 11678 L | 9000 L | (LxWxH)-(2500x2000x2580) | 2 Nos x 1 1/2 inch | 2 Nos x 3 inch | 2 Nos x 3 inch | 2 Nos x 1 inch
REF NO. | LOCATION | SERVING | SYSTEM | PUMP |  |  |  |  | ELECTRICAL |  |  |  |  | REMARKS
|  |  |  | TYPE | QTY (Nos.) | CAPACITY Kg/s | SET SIZE | HEAD (kPa) | RATED POWER kW | DETAILS V / PH / HZ | STARTER | DUTIES @ RPM | SOURCE
BCWP 01 | Basement | PH Plantroom | PH | Vertical Inline Pump set | 3 | 4.4 | 1370 (W) x 1040 (D) x 1460 (H) | 1050 | 5.5 | 380 / 3 / 50 | VFD | 3250 | Normal | Grundfos Run, Assist & Stand By pump skid mounted along with panel
REF | LOCATION | DESCRIPTION | MODEL | DESIGN FLOW RATE | CAPACITY | FILTRATION RATING | SYSTEM CONNECTION (DN) | MAXIMUM OPERATING PRESSURE | DIFFERENTIAL PRESSURE SWITCH | ACTUATOR | ELECTRICAL |  | REMARKS
[11 empty] | UNIT POWER INPUT | POWER SUPPLY
[11 empty] | kW | (V/Ph/Hz)
SCWC 101 | BCWS | Mediagon Physical Water Conditioner | Goodwater GWM300/CU | - | 65000 L/HR | - | 76 | - | - | - | - | - | SIZE - (L x D x H - 200 x 120 x 200)
RRF 101 | MCWS | Reverse Rinse Filters | Goodwater RRF F78TS-300 | 3 L/S | - | 20µ | 80 | 16 BAR | DDS76-1 | Z11AS | 0.01 | 1 / 230 / 50 | SIZE - (H x h x F x D x L - 665 x 508 x 200 x 230 x 310)
UV 101 | BCWS | UV Disinfection Unit | Goodwater Tucana VSL 7 | 4 L/S | - | - | 1˝ | 16 BAR | - | - | 0.23 | 1 / 230 / 50 | SIZE - (A x B x C x D x E- 129 x 167 x 103 x 1155 x 1041)