## Sheet1
Camden Energy & Sustainability Comments |  |  |  |  | Design Team Response
Issue | Comments | Issue | Action | Draft Condition / s106 Wording | Owner | Response
Carbon Reductions | The reported carbon emissions are confirmed by the GLA carbon emissions reporting spreadsheet in Appendix B.3 (p1287 and p1284. From Tables in the report • Overall carbon reduction of 59.52% for the residential areas exceeds the requirement for 35% minimum on site • Overall carbon reduction of 39.6% for the non-residential areas meets the requirement for 35% minimum on site • Overall carbon reduction of 58.81% site wide does not meet the requirement for net zero carbon and therefore a carbon offset payment of £184,224 is required (64.64 tonnes £95 per tonne for 30 years) • A reduction of 11.9% in carbon emissions through energy efficiency measures at Be Lean stage meets the requirement of 10% for residential • A reduction of 25.38% in carbon emissions through energy efficiency measures at Be Lean stage meets the requirement of 15% for commercial • A reduction of 54.05% in carbon emissions at Be Green stage for the residential areas meets the requirement of 20% from onsite renewable energy • A reduction of 19.06% in carbon emissions at Be Green stage for the non-residential areas does not quite meet the requirement of 20% from onsite renewable energy however the target is met overall on site with a 52.99% reduction | A carbon offset payment of £184,224 should be secured through s106. | Secure through s106 | None provided. | AECOM | Carbon emission figures stated are corrected, as per Energy Strategy. S106 wording to be provided for review and comment.
Be Lean | The proposals achieve good levels of energy efficiency through design with good insulation, low air permeability and low energy lighting. | No Issue | No action | None provided. | - | No response required.
Energy Use Intensity | Energy Demand information has been provided but has not been provided in the format requested by the GLA energy assessment guidance as Energy use intensity and Space heating by m2. | EUI information should be provided and shown to be within the benchmarks from table 4 of the GLA energy assessment guidance | Further information required. | None provided. | AECOM | The GLA Energy Assessment Guidance, including EUI and Space Heating was introduced in June 2022. The Energy Statement was produced in May 2022 and planning application submitted on 5th May 2022. In addition, the GLA website (accessed 17/08/2022) currently states:“Part L 2021 of national building regulations took effect on 15 June 2022 and the Energy Assessment Guidance and Carbon Emissions Reporting Spreadsheet have been updated accordingly. A cover note to accompany the guidance has also been published to explain the key changes. However, as the accompanying Part L 2021 software is not yet available, planning applicants should continue to use the 2020 guidance, spreadsheet and the Part L 2013 methodology until the software has been approved by government and is fully functional. This webpage will be updated as more information on the software timings become available.” At the time of writing (17/08/2022), the new approved SAP 10.2 calculation software is still not fully functioning and is having technical errors which means it cannot produce Emission Rate (ER) and Primary Energy Rate (PER) results. Given the date of the planning application and GLA website statement on continuing to use the 2020 Energy Assessment guidance, we have not undertaken or reported EUI and Space Heating Demand.
Be Clean | No comments | Future proofing including space for plant and soft points for connection to District Heating to be secured through s106 | Secure through s106 | None provided. | AECOM | S106 wording to be provided for review and comment.
Be Green | Communal heat pump led heat network with low temp hot water loop to provide 95% of heat demand. A total of 163 solar PV panels with total 57.05kWp is proposed. However it is not clear if solar PV has been maximised as large parts of the roof space seem to be empty but this may be due to overshadowing. | Solar PV details to be secured through condition to include at least 163 solar PV panels and 57kWp and consideration of feasibility of additional capacity, combining with green roof, overshadowing assessment and maintenance plan | Condition recommended. | Solar PV and green roofs: Prior to commencement of development other than site clearance & preparation, a feasibility assessment including overshadowing assessment and maintenance plan with the aim of maximising the provision of solar photovoltaics and green roofs with a minimum substrate of 150mm, to include at least 163 Solar PV panels providing 57kWp, should be submitted to the local planning authority and approved in writing. The buildings shall not be occupied until the approved details have been implemented and these works shall be permanently retained and maintained thereafter. Reason: To ensure the development provides adequate on-site renewable energy facilities and contributes to minimising the need for further water infrastructure in an area of water stress in accordance with policies CC2 and CC3 of the London Borough of Camden Local plan Policies | AECOM | Correct, PV has not been proposed to the lower roof levels due to overshadowing and space allocation for roof mounted plant. Substrate depth should be removed from draft on-site renewable energy condition wording. Reason for condition to be revised as currently refers to water infrastucture.
Be Seen |  | Reporting to be secured through condition or s106 | Condition or S106 recommended | ‘Be Seen’ energy monitoring – draft wording for legal agreements ‘Be Seen’ energy monitoring Clauses a) Prior to each Building being occupied, the Owner shall provide updated accurate and verified ‘as-built’ design estimates of the ‘Be Seen’ energy performance indicators for each Reportable Unit of the development, as per the methodology outlined in the ‘As-built stage’ chapter / section of the GLA ‘Be Seen’ energy monitoring guidance (or any document that may replace it). All data and supporting evidence should be submitted to the GLA using the ‘Be Seen’ as-built stage reporting webform (https://www.london.gov.uk/what-we[1]do/planning/implementing-london-plan/london-plan-guidance-and-spgs/be-seen-energy[1]monitoring-guidance). The owner should also confirm that suitable monitoring devices have been installed and maintained for the monitoring of the in-use energy performance indicators, as outlined in the ‘In-use stage’ of the GLA ‘Be Seen’ energy monitoring guidance document (or any document that may replace it). b) Upon completion of the first year of Occupation or following the end of the Defects Liability Period (whichever is the later) and at least for the following four years after that date, the Owner is required to provide accurate and verified annual in-use energy performance data for all relevant indicators under each Reportable Unit of the development as per the methodology outlined in the ‘In-use stage’ chapter / section of the GLA ‘Be Seen’ energy monitoring guidance document (or any document that may replace it). All data and supporting evidence should be submitted to the GLA using the ‘Be Seen’ in-use stage reporting webform (https://www.london.gov.uk/what-we-do/planning/implementing-london[1]plan/london-plan-guidance-and-spgs/be-seen-energy-monitoring-guidance). This obligation will be satisfied after the Owner has reported on all relevant indicators included in the ‘In-use stage’ chapter of the GLA ‘Be Seen’ energy monitoring guidance document (or any document that may replace it) for at least five years. c) In the event that the ‘In-use stage’ evidence submitted under Clause b) shows that the ‘As-built stage’ performance estimates derived from Clause a) have not been or are not being met, the Owner should investigate and identify the causes of underperformance and the potential mitigation measures and set these out in the relevant comment box of the ‘Be Seen’ in-use stage reporting webform. An action plan comprising measures identified in Clause b) shall be submitted to and approved in writing by the GLA, identifying measures which would be reasonably practicable to implement and a proposed timescale for implementation. The action plan and measures approved by the GLA should be implemented by the Owner as soon as reasonably practicable. Definitions “Defects Liability Period” means such period of time following Practical Completion of a Building in which a contractor may remedy defects as may be included in the building contract for the relevant Building; “Reportable Unit” means a Reportable Unit (Energy Centre), Reportable Unit (Residential) or Reportable Unit (Non-Residential); “Reportable Unit (Energy Centre)” means either a connection to a third-party District Heating Network, a self-contained Energy Centre serving multiple residential/non-residential properties (within the Site) or a self-contained energy system serving multiple residential properties (within a Block or Building); “Reportable Unit (Residential)” means an individual Block or Building of five or more flats or a group of five or more houses; “Reportable Unit (Non-Residential)” means a Building with a single occupier/tenant (including block of flats' communal areas) or a Building with multiple tenants; | Wates / Camden | Be Seen s106 wording to be reviewed and commented upon by Wates & Camden
Overheating | The Overheating Assessment states that “site acoustic constraints prevent windows opening on approximately 86% of the units”. It also states that “A temperature lopping solution was tested. This introduced a small amount of limited cooling to the spaces via a MVHR unit and was only considered to be active when room environment exceeded the upper threshold of 25°C.” Further 6.3 states “Option 2 was the base run without any site constraints, i.e. with no noise or security limitations, in order to demonstrate that the design performs well with the passive measures that have been implemented.” Further “Option 3 implemented the suggested improvements in the failing rooms of option 2. This resulted in 26 out of the 27 sample units achieving a pass, which translated to an approximate sample unit pass rate of 96%. The measures suggested in option 2 were sufficient to mitigate the overheating in the failing bedrooms and mid floor living room. However, the top floor living room still failed the TM59 assessment due to greater solar exposure. If a pass is required, we would recommend considering the above suggested improvements.” Modelling has been undertaken to show that without noise or security limitations the design and passive measures would prevent overheating – 85% of the samples achieved a pass. If the measure for option 3 are included this increases to 96%. | If the measures for Option 3 are incorporated to minimised cooling demand and achieve a pass then due to the noise and security constraints the proposed temperature lopping via MVHR is considered an efficient way to actively prevent overheating and would be acceptable in this circumstance | Confirmation of measures in option 3 incorporated into the design. | None provided. | AECOM | Yes, Option 3 is incorporated into the design.
Water Efficiency | The sustainability statement states “The water fixtures and fittings specified for each home will collectively deliver no more than 105 litres/person/day per home (as calculated for Building Regulations Approved Document G)” | Water efficiency target to be conditioned | Condition recommended | Water efficiency condition: The development hereby approved shall achieve a maximum internal water use of 105 litres/person/day, and 5 litres/person/day for external water use. The dwelling/s shall not be occupied until the Building Regulation optional requirement has been complied with. Reason: To ensure the development contributes to minimising the need for further water infrastructure in an area of water stress in accordance with policies CC1, CC2 and CC3 of the London Borough of Camden Local Plan Policies and Policy SI 5 of the London Plan 2021. | AECOM | Proposed condition wording is reasonable.
BREEAM | The ground floor commercial areas of the development should achieve BREEAM Excellent with at least 60% of the available credits in Energy and Water and 40% of the credits for materials. | A BREEAM pre assessment should be undertaken | Further information required. | None provided. | AECOM | Camden Local Plan Policy CC2 states that BREEAM ‘Excellent’ rating’s are expected for non-domestic developments over 500sqm from 2019. Camden Planning Guidance (Jan 2021): Energy Efficiency and Adaptation, Section 11 states that “BREEAM Excellent is required for all non-residential development of 500sqm or more floorspace”. The proposed floor area of the non-domestic units are 305sqm, therefore under the threshold to undertake a BREEAM assessment.
Home Quality Mark | The Council will be supportive of scheme that aim to achieve HQM, subject to other policy and design considerations. | Achievement of HQM 4 star welcomed and to be secured through condition or s106 | Condition / s106 recommended | None provided. | AECOM | Condition wording to be provided for review and comment.
Whole Life Carbon | The proposals meet the aspirational benchmarks for whole life carbon for residential buildings. | Applicants should provide post construction information. | Condition recommended | None provided. | AECOM | Condition wording to be provided for review and comment.
Circular Economy | The key commitments of the Applicant are: • To target diversion of a minimum of 95% of non-hazardous demolition waste from landfill for reuse, recycling or recovery; • To target diversion of a minimum of 95% of inert excavation waste generated from the Proposed Development from landfill for beneficial use; • To target diversion of a minimum of 95% of construction waste generated by the Proposed Development from landfill for reuse, recycling or recovery; • To facilitate recycling levels in operation which will exceed the municipal waste recycling target of 65% by 2030; and • To specify a minimum 20% of the total value of the selected products and materials to include recycled and reused content; and • Wates Residential to provide a Post-Construction report to the Greater London Authority A pre redevelopment audit has been undertaken, design approached and principles considered, bill of materials estimated and a commitment has been made to the required targets for 95 per cent reuse/recycling/recovery of construction and demolition waste and for 95 per cent of excavation to be put to beneficial use which meets the requirements. | The achievement of the commitments in the Circular Economy Statement including the waste diversion and recycling targets should be conditioned. A post construction monitoring report is required. | Conditions recommended | Post Construction and Demolition Waste: Delivered in accordance with details. The Circular Economy Statement as approved (Circular Economy Statement by Aecom 7th June 2022 ver 5) shall be delivered to achieve at least 95% reuse/recycling/recovery of construction and demolition waste and 95% beneficial use of excavation waste. Reason: To ensure all development optimise resource efficiency in accordance with policy CC1 of the London Borough of Camden Local Plan Policies and to reduce waste and support the circular economy in accordance with policy SI 7 of the new London Plan. Construction monitoring report Prior to the occupation [of the development/each phase of development], a post construction monitoring report should be completed in line with the GLA’s Circular Economy Statement Guidance. The post-construction monitoring report shall be submitted to the GLA, currently via email at: circulareconomystatements@london.gov.uk, along with any supporting evidence as per the guidance. Confirmation of submission to the GLA shall be submitted to, and approved in writing by, the local planning authority, prior to occupation of the [development/ phase of development]. Reason: In the interests of sustainable waste management and in order to maximise the re-use of materials | AECOM | The CES states that will target diversion of at least at least 95% reuse/recycling/recovery of construction and demolition waste and 95% beneficial use of excavation waste. As per GLA gudiance, we would recommend CE statement would be received three months post-construction. Planning Stage CES accounts for the whole development so suggest post construction monitoring report also done for whole development, to ensure directly comparable reporting is provided.