|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Matthew Dempsey, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 22 September 2022 |
| Re: | 20 Triton Street London NW1 3BF |
| Proposal: | Installation of louvres at level 2 |
| Reference: | Planning application ref. 2022/3491/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

An acoustic assessment has been submitted in support of a planning application in relation to the proposed Installation of louvres at level 2 at Installation of louvres at level 2.

The nearest noise sensitive receptors have been identified as to the north of the site are the residential apartments on Triton Square and the commercial properties on Triton Street .

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, Camden Council’s Local Plan, version June 2017 and BS 4142:2014.

The plant noise criteria have been adequately predicted  taking into consideration distance losses, surface acoustic reflections and, where applicable, screening provided by the building.

The plant noise impact assessment has found that installation of the proposed louvres will enabled compliance to the correct planning policy requirements stipulated by the Local Authority and should not have an adverse impact on the nearest sensitive receivers.

I am satisfied that the submitted acoustic submission meets our local plan guidelines and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

In respect of any proposed louvre installation, the applicant shall ensure that the existing background noise level is not increased when measured one metre from the nearest noise sensitive elevation. In order to achieve this the installation must be designed / selected or the noise attenuated so that it is10dB below the existing background level. This will maintain the existing noise climate and prevent ‘ambient noise creep’

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967 652382