|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Matthew Dempsey, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Camilo Castro-Llach (Noise Officer) |
| Date: | 01 Augst 2022 |
| Re: | 5 Bloomsbury Place London WC1A 2QP |
| Proposal: | Replacement of existing gas fired boiler with Air Source Heat Pumps, including 3 external units and 19 corresponding internal units. |
| Reference: | Planning application ref. 2022/1635/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

The applicant seeks to replace the existing gas fired central heating system with Air Source Heat Pumps and associated internal heating / cooling units at 5 Bloomsbury Place, London. An acoustic assessment has been submitted in support of the application,

The property is situated between Bloomsbury Square and Southampton Row on

the north side of Bloomsbury Place. There are no residential dwellings overlooking the proposed plant, with the adjacent commercial  premises at 4 Bloomsbury Place being the most affected non-residential sensitive receptor.

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, Camden Council’s Local Plan, version June 2017, BS 8233:2014 and BS 4142:2014.

The plant noise levels have been adequately predicted at the at the identified receptors taking into consideration distance losses, surface acoustic reflections and, where applicable, screening provided by the building.

Calculations show that noise emissions from the proposed units ,with mitigation measures included, would be sufficiently low as to cause no negative impact on nearby noise sensitive non-residential sensitive receptor, therefore meeting the Camden London Borough Council’s requirements.

The noise impact assessment recommends that a 3 sided enclosure be introduced between the plant installation and the noise sensitive receivers.

I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

The external noise level emitted from plant, machinery or equipment at the development hereby approved shall be lower than the lowest existing background noise level by at least 10dBA, by 15dBA where the source is tonal, as assessed according to BS4142:2014 at the nearest and/or most affected noise sensitive premises, with the machinery operating at maximum capacity. A 3 sided acoustic enclosure shall be introduced between the external units and the noise sensitive receivers.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017.

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

If you have any queries, please do not hesitate to contact me.

Regards

Camilo Castro-Llach

Noise Officer

Supporting Communities

London Borough of Camden