|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Sofie Fieldsend, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 27 October 2022 |
| Re: | 61 Redington Road London Camden NW3 7RP |
| Proposal: | Conversion of 3x flats (2B4P) to 2x flats (1B2P and 5B10P). Erection of four storey rear extension at lower ground to 2nd floor including excavation at lower ground and front lightwells. Roof extension. Erection of rear ground floor terrace. Installation of 2x ASHP and 1 air con unit in rear garden and landscaping alterations |
| Reference: | Planning application ref. 2022/1962/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

An acoustic assessment has been submitted in support of the proposed renovation of residential dwellings, and a noise impact assessment of associated plant, at 61 Redington Road, London.

It is proposed that 2no. heat pumps and a single air conditioning unit (ACU) will be located at the bottom of the garden and housed within an acoustic enclosure.

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, Camden Council’s Local Plan, version June 2017 and BS 4142:2014.

We would expect to see the following standards achieved internally:

| Activity | Location | 07:00 to 23:00 | 23:00 to 07:00 |
| --- | --- | --- | --- |
| Resting | Living Room | 35 LAeq, 16hour | - |
| Dining | Dining Room / Area | 40 LAeq, 16hour | - |
| Sleeping (daytime resting) | Bedroom | 35 LAeq, 16hour | 30 LAeq, 8hour 45 LAfmax |

- These levels are derived in part from Table 4 of BS8233:2014 and also World Health Organization figures.  The figures from BS8233:2014 are themselves derived from World Health Organization values.

- The notes to Table 4 of BS8233:2014 apply to the interpretation of the above figures.

- It is also expected that to achieve an acceptable internal noise climate that individual noise events shall not exceed 45dB LAFmax on a frequent basis. The acceptability of the frequency of events will depend on the level of exceedance of the 45dB LAFmax criteria. Up to 10 events may be acceptable for small exceedances (<5dB) whilst for high exceedences (>=5 dB and <10 dB) less than 5 events will be acceptable. Events in excess of 10 dB above 45 dB are not permitted.

The maximum day time noise level in outdoor living areas exposed to external road traffic noise should not exceed 50dBA Leq 16 hour [free field].

Having reviewed the acoustic information by Noise Solution Ltd, document ref: 90538/EBF dated  20th April 2022 , I am satisfied that appropriate acoustic façade design and an appropriate ventilation staregy has been considered.

The plant noise impact assessment has also found that installation of the proposed ASHPs, when appropriately attenuated as proposed, should comply to the correct planning policy requirements stipulated by the Local Authority and should not have an adverse impact on the nearest sensitive receivers.

The plant noise criteria have been adequately predicted  taking into consideration distance losses, surface acoustic reflections and, where applicable, screening provided by the building.

I am satisfied that the submitted acoustic submission meets our local plan guidelines for the most part and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

The design and structure of the development shall be of such a standard that it will protect residents within it from existing external noise so that they are not exposed to levels indoors of more than 35 dB LAeq 16 hrs daytime and of more than 30 dB LAeq 8 hrs in bedrooms at night.  No dwelling shall be occupied until the approved sound insulation and ventilation measures have been installed to that property in accordance with the approved details.  The approved measures shall be retained thereafter in perpetuity.

Reason: To ensure that the amenity of occupiers of the development site is not adversely affected by noise from transport and commercial noise sources in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

In respect of any proposed air conditioning, mechanical ventilation or associated plant, the applicant shall ensure that the existing background noise level is not increased when measured one metre from the nearest noise sensitive elevation. In order to achieve this the plant must be designed / selected or the noise attenuated so that it is 10dB below the existing background level. This will maintain the existing noise climate and prevent ‘ambient noise creep’

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to commencement of the development, details shall be submitted to and approved in writing by the Council, of an enhanced  sound insulation value DnT,w [and L’nT,w] of at least 5dB above the Building Regulations value, for the floor/ceiling/wall structures separating different types of rooms/ uses in adjoining dwellings, namely [eg. living room and kitchen above bedroom of separate dwelling].  Approved details shall be implemented prior to occupation of the development and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

At least 21 days prior to the commencement of any site works, all occupiers surrounding the site should be notified in writing of the nature and duration of works to be undertaken. The name and contact details of a person responsible for the site works should be made available for enquiries and complaints for the entire duration of the works and updates of work should  be provided regularly. Any complaints should be properly addressed as quickly as possible.

No waste materials should be burnt on site of the development hereby approved.

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967 652382