## Sheet1
GEM ENVIRONMENTAL BUILDING SERVICES LTD NON-DOMESTIC COMMISSION RECORD
Serial No.
Registered Business/engineer details can be checked at www.gassaferegister.co.uk or by calling 0800 408 5500
Work activity: commissioning/service/maintenance (Delete as appropriate)
Gas safe is a registered trade mark of HSE and is used under license.
| Details of Registered Business |  |  |  |  | Appliance Details |  |  |  | No.1 |  |  |  | No.2 |  |  | No.3 |  | No.4
| Gas Safe Register No |  |  | 182887 |  | Location |  |  |  | Boiler Room |  |  |  | Boiler Room |  |  | Boiler Room |  | Boiler Room
[6 empty] | Type |  |  |  | Sectional |  |  |  | Sectional |  |  | Sectional |  | Sectional
| Registered Engineer's Name |  | G Sey
[6 empty] | Make |  |  |  | Ideal |  |  |  | Ideal |  |  | Ideal |  | Ideal
| Gas Safe Register License Number |  |  |  |  | Model |  |  |  | Imax Xtra E280 |  |  |  | Imax Xtra E280 |  |  | Imax Xtra E280 |  | Imax Xtra E280
[6 empty] | Serial No. |  |  |  | vr 20243900000220 1912 |  |  |  | vr 20243900000230 1924 |  |  | vr 20243900000245 1929 |  | vr 20243900000247 1929
| Business | GEM ENVIRONMENTAL BUILDING SERVICES LTD
[6 empty] | Age approximate |  |  |  | 1 |  |  |  | 1 |  |  | 1 |  | 1
| Address | 121-122 OMEGA WORKS |  |  |  | Burner manufacturer (if different) |  |  |  | N.A |  |  |  | N.A |  |  | N.A |  | N.A
Type
[6 empty] | Type of Flue |  |  |  | F.D. |  |  |  | F.D. |  |  | F.D. |  | F.D.
|  | 4 ROACH ROAD, LONDON |  |  |  | Model
| Postcode | E3 2PF
[6 empty] | Combustion Checks | [9 empty] | Supporting checks (Yes/No/NA) |  |  | No.1 | No.2 | No.3 | No.4
| Contact No | 020 8985 0409
[6 empty] | Appliance No. |  | No. 1 |  | No.2 |  | No.3 |  | No.4 |  | Flue flow test satisfactory? |  |  | Y | Y | Y | Y
[6 empty] | Firing Mode |  | Low | High | Low | High | Low | High | Low | High | Spillage test satisfactory? |  |  | Y | Y | Y | Y
| Details of Site |  |  |  |  | Heat input rating (kW) |  |  | 310.9 |  | 310.9 |  | 310.9 |  | 310.9 | Air/gas pressure switch operating correctly? |  |  | Y | Y | Y | Y
[6 empty] | Gas burner pressure (mbar) |  | - | - | - | - | - | - | - | - | Safety devices operating correctly? (Yes/No) |  |  | Y | Y | Y | Y
Name (Mr/Mrs/Miss/Ms)
[6 empty] | Gas rate (m³/hr) | [9 empty] | Burner lock-out time (in seconds) |  |  | <5 | <5 | <5 | <5
Heat input rating (kW)
| Address | Kiln Place Estate |  |  |  | Air/gas ratio control setting | [9 empty] | Temperature and limit thermostats operating correctly? |  |  | Y | Y | Y | Y
Gas rate (m³/hr)
[6 empty] | Ambient temperature (°C) |  | 21 | [7 empty] | Chimney system installed in accordance with appropriate standards? (Yes/No) |  |  | Y | Y | Y | Y
1-64 Kiln Place
[6 empty] | Flue gas temperature (°C) |  | 51 | 60 | 47 | 57 | 45 | 57 | 49 | 4 | Fan-flue interlock operating correctly? |  |  | N.A. | N.A. | N.A. | N.A.
Flue gas temperature net (°C)
| Kentish Town |  |  |  |  | Flue gas temperature net (°C) | [9 empty] | Appliance serviced? |  |  | N | N | N | N
[6 empty] | Flue draught pressure (mbar) | [9 empty] | Gas booster(s)/compressor(s) operating correctly? |  |  | N.A. | N.A. | N.A. | N.A.
| London |  |  |  |  | Oxygen (O2) %
[6 empty] | Oxygen (O2) % |  | 4.2 | 3.8 | 4.2 | 3.9 | 4.5 | 3.8 | 4.1 | 4 | Gas installation pipework adequately supported/identified? |  |  | Y | Y | Y | Y
| Postcode | NW5 4AP |  |  |  | Carbon Monoxide (CO) ppm |  | 6 | 54 | 6 | 64 | 0 | 0 | 0 | 0 | Gas installation pipework sleeved/labelled as necessary? |  |  | Y | Y | Y | Y
[6 empty] | Carbon Dioxide (CO2) % |  | 9.5 | 9.7 | 9.5 | 9.7 | 9.4 | 9.7 | 9.6 | 9.7
| Contact No |  |  |  |  | NOX %
NOX %
Ventilation type/checks Non room sealed appliance (Detail in 1. or 2. below)
Excess air %
| Details of Customer/Landlord (or agent where appropriate) |  |  |  |  | CO/CO2 – Ratio |  | 0 | 0.0005 | 0 | 0.0006 | 0 | 0 | 0 | 0
1. Natural ventilation
[6 empty] | Gross efficiency % |  | 89 | 88 | 89 | 88 | 89 | 88 | 89 | 89
| Name (Mr/Mrs/Miss/Ms) |  |  |  |  | NOX % | [9 empty] | Ventilation size: |  | High-level free area (cm²) |  |  | 24000
CO flue dilution ppm
[6 empty] | CO/CO2 - Ratio | [11 empty] | Low-level free area (cm²) |  |  | 4000
Address
2. Mechanical ventilation
[6 empty] | Safety Information |  |  |  |  | Yes/No |  | If Warning/Advisory Record Issued, Insert Serial No*
[16 empty] | Flow rate |  | inlet (m³/s) |  |  | -
[6 empty] | Has a Warning/Advisory Record been issued? |  |  |  |  | No
[18 empty] | outlet (m³/s) |  |  | -
[6 empty] | Have warning labels been affixed? |  |  |  |  | No
| Postcode | [14 empty] | Interlock fitted |  | Yes/No/NA |  |  | N.A.
[6 empty] | Has a responsible person been advised? |  |  |  |  | Yes
| Contact No | [14 empty] | Interlock operating correctly |  | Yes/No/NA |  |  | N.A.
[16 empty] | Room sealed applicable |  | Yes/No |  |  | No
| Brief description of work carried out and/or Remedial works required |  |  |  |  | Declaration of Gas Safety – I confirm that this record is a true and accurate representation of the gas work carried out on the day of inspection. Relevant and appropriate duty-holders are required to ensure that gas appliances, installation pipework and flues are maintained in a safe condition so as to prevent the risk of injury to any person.
[16 empty] | Is ventilation satisfactory? |  | Yes/No |  |  | Yes
Commission boilers as per manufacturer's instructions. Gas meter not working correctly, so unable to gas rate. Fan speeds and co2 figures are as per design spec.
Ventilation Room sealed appliance
Gas Safe Engineer's signature:
|  |  | PASS | FAIL
| Gas Drop Test |  | Pass | [12 empty] | Appliance ventilation satisfactory |  | Yes/No |  |  | -
[6 empty] | Date: | 2019-12-11
| Appliance Service |  | Yes | [12 empty] | Plant Room ventilation satisfactory |  | Yes/No/NA |  |  | -
ISSUED BY GEM IN PARTNERSHIP WITH CAMDEN