## Sheet1
commercial gas testing and purging record
REGISTERED BUSINESS DETAILS Reg No: |  |  | 219117 | DECLARATION OF GAS SAFETY
Gas engineer: | G R Sey |  |  | I confirm that all the work described by me on this form has been satisfactorily completed in accordance with the current gas safety regulations, industry standards and procedures.
Eng no: | 4495314
Company: | GEM EBS
Address: | Level 37, One Canada Square,
| Canary Wharf, London |  |  | Engineers signature: |  |  |  | Date: | 11/12/19
Postcode: | E14 5AB | Tel No: | 02089850409
INSPECTION/INSTALLATION ADDRESS |  |  |  | CUSTOMER'S NAME & ADDRESS
Name: | Kiln Place Estate Boiler Room |  |  | Name:
Address: | Kiln Place |  |  | Address:
Postcode: | NW5 4AW | Date: | 11/12/19 | Postcode: |  |  | Tel:
WORK CARRIED OUT: TIGHTNESS TEST |  | X | PURGE | X | STRENGTH TEST
DETAILS OF TIGHTNESS TEST |  |  | DETAILS OF PURGING PROCEDURE |  | DETAILS OF STRENGTH TEST
Natural Gas or LPG |  | NG | Has a risk assessment been carried out? | Y |  | Components not suitable for Strength testing have been removed
Installation new (N)/ new extension(NE)/ existing (E) |  | N | Has a procedure for the purge been documented | Y
Weather/temperature stable? |  | Y | Have warning signs (e.g.No Smoking) been displayed | Y |  | Installation new/new extension/existing
Meter Type (e.g. Rotary,Diaphragm) |  | N.A. | Have all persons nearby been advised accordingly | Y |  | Test Method hydrostatic/pneumatic
Meter Designation (e.g. U6, P7) |  | N.A. | Have all valves involved been labelled | Y |  | Strength Test Pressure mbar/bar
Has a meter by-pass been installed? |  | N.A. | Have nitrogen cylinders been checked for correct content | N.A. |  | Test Medium air/nitrogen/water
Installation Volume:(IV) Gas Meter |  | N.A. | Are suitable fire extinguishers available | Y |  | Stabilisation Period (in minutes)
Installation Volume Pipework and Fittings |  | 0.162 | Are two-way radios (intrinsically safe) available | Y |  | Strength Test Duration (in minutes)
Total IV |  | 0.162 | Are all necessary electrical bonds fitted | Y |  | Calculated Pressure Drop mbar/bar
Test Medium (gas or air) |  | GAS | Installation Pipework and Fitting Volume (m^3) | 0.162 |  | STRENGTH TEST RESULTS
Tightness Test Pressure in mbar |  | 25 | Gas Meter Volume (m^3) | 0 |  | Actual Pressure Drop
Pressure Gauge (u-tube/electronic) |  | ELEC. | Calculated Purge Volume: (Pipework and Fittings, m^3) | 0.243 |  | Strength Test Pass/Fail
MPLR Maximum Permitted Leak Rate (m^3/hr) |  | 0.0014 | Total Purge Volume: (m^3) | 0.243 |  | NOTIFICATION OF UNSAFE GAS INSTALLATION!
Let By Test Period (in minutes) |  | 2 | Is gas detector intrinsically safe | Y |  | This installation and must not be used until the issues detailed in additional comments/works required are carried out by a competent person.
Stabilisation Period (in minutes) |  | 2 | Is oxygen measuring device intrinsically safe | Y
TTD Tightness Test Duration (in minutes) |  | 2
Are there any areas with inadequate ventilation? Y/N |  | N |  |  |  | Engineers signature:
Is barometric pressure correction required? Y/N |  | N
TIGHTNESS TEST RESULTS |  |  | PURGE TEST RESULTS
Actual Pressure Drop (if any) |  | 0 | Proceed with purge recording final test criteria readings O2% or LFL% | 100% lfl |  | Responsible Person:
Actual Leak Rate (m^3/hr) |  | 0
Areas with inadequate ventilation checked? |  | Y | Purge Test Pass/Fail | Pass
Tightness Test Pass/Fail |  | PASS
ADDITIONAL COMMENTS/WORKS REQUIRED