## To-do list
Checklist for commission and service
Pump Commissioning
| Customer |  | GEM EBS LTD
| Equipment type model |  | BOILER SHUNT PUMPS
| Site reference |  | KILN PLACE CAMDEN
| Reason for visit |  | Commissioning
| Date |  | 2020-02-04
Done? | Performance data | Due By | Notes
a | Description of unit and serial number |  | LOWARA XL PLUS 50-120F x 4 20181210
a | Power Supply |  | 230V 1ph
a | Check power supply |  | Good 230V
a | Check operation of inverter |  | Good
a | Program inverter |  | Via LCD display screen
a | Set point |  | 7.5 Metres
a | Inverter model |  | Integral Lowara Inverter
a | Pump FLC |  | 0.4 - 4.0 Amps
a | System Type |  | Heating Pumps
a | Motor Output |  | 892 WATTS
a | Speed of Motor |  | 360 - 3600 rpm
Remarks
All 4 pumps set as the same for boilers 1-4, all working well.
Engineer J Brown

## Sheet1
Service | LTHW
Commissioning | CHW
Call out/Maint | MTHW
Warranty | SECONDARY