## Weather data
|  | Dry-bulb temperature (°C) |  |  | Var. Name |  | Location | Min. Val. | Min. Time | Max. Val. | Max. Time | Mean |  |  |  | Q | 5041.7539 | kWh / year
[5 empty] | Dry-bulb temperature |  |  | -3.7 | 05:00,26/Nov | 34.6 | 18:00,22/Jul | 13.03 |  |  |  | School Area | 345 | m2
Date | Time | London_LHR_DSY1_2020High50.epw |  |  | Vent Profile | System On / off? | supply air temp | Air off Heat Exchanger | Heating Coil Air Delta T | Air Volume [m3/s] | Q vent air KWh | Infiltration [ACH] | Volume [m3] | Q infiltration KWh | Building Thermal Load | Vent Heating Demand | 14.6138 | kWh/ m2/ year
Sat, 01/Jan | 24:00 | 8.5 | Sat | WE | Off | OFF | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 1:00 | 8.6 | Sat | WE | Off | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 2:00 | 8.5 | Sat | WE | Off | OFF | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 3:00 | 9.2 | Sat | WE | Off | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 4:00 | 8.6 | Sat | WE | Off | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 5:00 | 8.4 | Sat | WE | Off | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 6:00 | 7.9 | Sat | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 7:00 | 8.6 | Sat | WE | On | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 8:00 | 8.3 | Sat | WE | On | OFF | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 9:00 | 7.9 | Sat | WE | On | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 10:00 | 7.9 | Sat | WE | On | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 11:00 | 8 | Sat | WE | On | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 12:00 | 8.8 | Sat | WE | On | OFF | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 13:00 | 9 | Sat | WE | On | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 14:00 | 9 | Sat | WE | On | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 15:00 | 8.8 | Sat | WE | On | OFF | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 16:00 | 8.7 | Sat | WE | On | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 17:00 | 8.4 | Sat | WE | On | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 18:00 | 8.5 | Sat | WE | On | OFF | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 19:00 | 7.9 | Sat | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 20:00 | 8 | Sat | WE | Off | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 21:00 | 7.9 | Sat | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 22:00 | 7.7 | Sat | WE | Off | OFF | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 23:00 | 7.5 | Sat | WE | Off | OFF | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
Sun, 02/Jan | 24:00 | 7.9 | Sun | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 1:00 | 7.9 | Sun | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 2:00 | 8 | Sun | WE | Off | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 3:00 | 7.9 | Sun | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 4:00 | 7.6 | Sun | WE | Off | OFF | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 5:00 | 7.7 | Sun | WE | Off | OFF | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 6:00 | 7.9 | Sun | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 7:00 | 7.9 | Sun | WE | On | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 8:00 | 7.6 | Sun | WE | On | OFF | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 9:00 | 7.7 | Sun | WE | On | OFF | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 10:00 | 7.5 | Sun | WE | On | OFF | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 11:00 | 7.9 | Sun | WE | On | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 12:00 | 8.2 | Sun | WE | On | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 13:00 | 8.4 | Sun | WE | On | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 14:00 | 8.8 | Sun | WE | On | OFF | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 15:00 | 8.9 | Sun | WE | On | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 16:00 | 8.8 | Sun | WE | On | OFF | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 17:00 | 8.3 | Sun | WE | On | OFF | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 18:00 | 7 | Sun | WE | On | OFF | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 19:00 | 6.6 | Sun | WE | Off | OFF | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 20:00 | 5.6 | Sun | WE | Off | OFF | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 21:00 | 4.4 | Sun | WE | Off | OFF | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 22:00 | 6.1 | Sun | WE | Off | OFF | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 23:00 | 6.6 | Sun | WE | Off | OFF | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
Mon, 03/Jan | 24:00 | 6.9 | Mon | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 1:00 | 7.3 | Mon | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 2:00 | 7.2 | Mon | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 3:00 | 6.9 | Mon | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 4:00 | 6.6 | Mon | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 5:00 | 6.3 | Mon | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 6:00 | 6 | Mon | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 7:00 | 5.9 | Mon | School Day | On | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 8:00 | 5.8 | Mon | School Day | On | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 9:00 | 6 | Mon | School Day | On | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 10:00 | 5.9 | Mon | School Day | On | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 11:00 | 6.1 | Mon | School Day | On | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 12:00 | 6.4 | Mon | School Day | On | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 13:00 | 6.7 | Mon | School Day | On | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 14:00 | 6.7 | Mon | School Day | On | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 15:00 | 6.8 | Mon | School Day | On | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 16:00 | 6.6 | Mon | School Day | On | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 17:00 | 6.6 | Mon | School Day | On | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 18:00 | 6 | Mon | School Day | On | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 19:00 | 6 | Mon | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 20:00 | 6 | Mon | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 21:00 | 6.2 | Mon | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 22:00 | 6.1 | Mon | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 23:00 | 6.7 | Mon | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
Tue, 04/Jan | 24:00 | 6.7 | Tue | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 1:00 | 7.1 | Tue | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 2:00 | 7.6 | Tue | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 3:00 | 7.8 | Tue | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 4:00 | 7.9 | Tue | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 5:00 | 7.9 | Tue | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 6:00 | 8 | Tue | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 7:00 | 8.6 | Tue | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 8:00 | 9.7 | Tue | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 9:00 | 10.2 | Tue | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 10:00 | 10.1 | Tue | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 11:00 | 10.6 | Tue | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 12:00 | 10.6 | Tue | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 13:00 | 11.6 | Tue | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 14:00 | 11.2 | Tue | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 15:00 | 10.8 | Tue | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 16:00 | 10.2 | Tue | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 17:00 | 8.9 | Tue | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 18:00 | 8.5 | Tue | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 19:00 | 8.2 | Tue | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 20:00 | 7.5 | Tue | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 21:00 | 6.9 | Tue | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 22:00 | 6.8 | Tue | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 23:00 | 6.5 | Tue | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
Wed, 05/Jan | 24:00 | 5.9 | Wed | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 1:00 | 4.5 | Wed | School Day | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 2:00 | 4.2 | Wed | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 3:00 | 3.8 | Wed | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 4:00 | 3.9 | Wed | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 5:00 | 3.5 | Wed | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 6:00 | 3.3 | Wed | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 7:00 | 2.9 | Wed | School Day | On | On | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 5.2763
| 8:00 | 2.2 | Wed | School Day | On | On | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 5.4697
| 9:00 | 3 | Wed | School Day | On | On | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 5.2487
| 10:00 | 4.2 | Wed | School Day | On | On | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 4.9172
| 11:00 | 5 | Wed | School Day | On | On | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 4.6962
| 12:00 | 6 | Wed | School Day | On | On | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 4.4199
| 13:00 | 6.7 | Wed | School Day | On | On | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 4.2266
| 14:00 | 7.3 | Wed | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 15:00 | 8.1 | Wed | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 16:00 | 8.8 | Wed | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 17:00 | 9.1 | Wed | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 18:00 | 9.2 | Wed | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 19:00 | 9.9 | Wed | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 20:00 | 10.5 | Wed | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 21:00 | 10.8 | Wed | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 22:00 | 11.2 | Wed | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 23:00 | 11.6 | Wed | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
Thu, 06/Jan | 24:00 | 11.5 | Thu | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 1:00 | 11.6 | Thu | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 2:00 | 11.3 | Thu | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 3:00 | 10.7 | Thu | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 4:00 | 9.8 | Thu | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 5:00 | 9.3 | Thu | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 6:00 | 9.8 | Thu | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 7:00 | 9.3 | Thu | School Day | On | On | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 3.5083
| 8:00 | 10.2 | Thu | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 9:00 | 9.5 | Thu | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 10:00 | 9 | Thu | School Day | On | On | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 3.5912
| 11:00 | 9.2 | Thu | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 12:00 | 9.8 | Thu | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 13:00 | 11.2 | Thu | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 14:00 | 11 | Thu | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 15:00 | 11 | Thu | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 16:00 | 10.8 | Thu | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 17:00 | 10.8 | Thu | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 18:00 | 10.7 | Thu | School Day | On | On | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 3.1216
| 19:00 | 10.7 | Thu | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 20:00 | 10.7 | Thu | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 21:00 | 10.3 | Thu | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 22:00 | 10.3 | Thu | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 23:00 | 10.1 | Thu | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
Fri, 07/Jan | 24:00 | 9.7 | Fri | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 1:00 | 9.8 | Fri | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 2:00 | 9.4 | Fri | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 3:00 | 9.5 | Fri | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 4:00 | 9.8 | Fri | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 5:00 | 9.5 | Fri | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 6:00 | 9.2 | Fri | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 7:00 | 9.8 | Fri | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 8:00 | 9.5 | Fri | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 9:00 | 9.7 | Fri | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 10:00 | 10.1 | Fri | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 11:00 | 10.1 | Fri | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 12:00 | 10.8 | Fri | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 13:00 | 11.5 | Fri | School Day | On | On | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 2.9006
| 14:00 | 11.8 | Fri | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 15:00 | 12.2 | Fri | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 16:00 | 12.2 | Fri | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 17:00 | 12.2 | Fri | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 18:00 | 12.2 | Fri | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 19:00 | 11.8 | Fri | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 20:00 | 11.7 | Fri | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 21:00 | 12.3 | Fri | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 22:00 | 12.3 | Fri | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 23:00 | 12.4 | Fri | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
Sat, 08/Jan | 24:00 | 11.7 | Sat | WE | Off | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 1:00 | 9.5 | Sat | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 2:00 | 9 | Sat | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 3:00 | 9.4 | Sat | WE | Off | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 4:00 | 9.2 | Sat | WE | Off | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 5:00 | 9.5 | Sat | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 6:00 | 9.5 | Sat | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 7:00 | 9.6 | Sat | WE | On | OFF | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 8:00 | 9.7 | Sat | WE | On | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 9:00 | 9.9 | Sat | WE | On | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 10:00 | 10 | Sat | WE | On | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 11:00 | 10.2 | Sat | WE | On | OFF | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 12:00 | 10.5 | Sat | WE | On | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 13:00 | 10.8 | Sat | WE | On | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 14:00 | 11.1 | Sat | WE | On | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 15:00 | 10.8 | Sat | WE | On | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 16:00 | 10.9 | Sat | WE | On | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 17:00 | 10.9 | Sat | WE | On | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 18:00 | 10.8 | Sat | WE | On | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 19:00 | 10.6 | Sat | WE | Off | OFF | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 20:00 | 10.5 | Sat | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 21:00 | 10.1 | Sat | WE | Off | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 22:00 | 10.2 | Sat | WE | Off | OFF | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 23:00 | 10.3 | Sat | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
Sun, 09/Jan | 24:00 | 10.3 | Sun | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 1:00 | 10.5 | Sun | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 2:00 | 10.5 | Sun | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 3:00 | 10.2 | Sun | WE | Off | OFF | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 4:00 | 9.9 | Sun | WE | Off | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 5:00 | 10 | Sun | WE | Off | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 6:00 | 10 | Sun | WE | Off | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 7:00 | 10.4 | Sun | WE | On | OFF | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 8:00 | 10.2 | Sun | WE | On | OFF | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 9:00 | 10.7 | Sun | WE | On | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 10:00 | 10.9 | Sun | WE | On | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 11:00 | 11 | Sun | WE | On | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 12:00 | 11.3 | Sun | WE | On | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 13:00 | 11 | Sun | WE | On | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 14:00 | 11.6 | Sun | WE | On | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 15:00 | 12 | Sun | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 16:00 | 11.8 | Sun | WE | On | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 17:00 | 11 | Sun | WE | On | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 18:00 | 11 | Sun | WE | On | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 19:00 | 11 | Sun | WE | Off | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 20:00 | 10.8 | Sun | WE | Off | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 21:00 | 10.5 | Sun | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 22:00 | 10.6 | Sun | WE | Off | OFF | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 23:00 | 10.5 | Sun | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
Mon, 10/Jan | 24:00 | 10.3 | Mon | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 1:00 | 10.2 | Mon | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 2:00 | 9.4 | Mon | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 3:00 | 8.8 | Mon | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 4:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 5:00 | 8.6 | Mon | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 6:00 | 8.2 | Mon | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 7:00 | 7.3 | Mon | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 8:00 | 6.6 | Mon | School Day | On | On | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 4.2542
| 9:00 | 6.3 | Mon | School Day | On | On | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 4.3371
| 10:00 | 5.9 | Mon | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 11:00 | 6.5 | Mon | School Day | On | On | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 4.2818
| 12:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 13:00 | 8.5 | Mon | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 14:00 | 8.2 | Mon | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 15:00 | 8.8 | Mon | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 16:00 | 9.1 | Mon | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 17:00 | 7.1 | Mon | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 18:00 | 5.5 | Mon | School Day | On | On | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 4.5581
| 19:00 | 5.1 | Mon | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 20:00 | 4.1 | Mon | School Day | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 21:00 | 4.2 | Mon | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 22:00 | 3.9 | Mon | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 23:00 | 3.2 | Mon | School Day | Off | Off | 22 | 20.12 | 1.88 | 1.7 | 3.591 | 0.25 | 1035 | 1.6024 | 0
Tue, 11/Jan | 24:00 | 2.4 | Tue | School Day | Off | Off | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 1:00 | 1.6 | Tue | School Day | Off | Off | 22 | 19.96 | 2.04 | 1.7 | 3.8966 | 0.25 | 1035 | 1.7388 | 0
| 2:00 | 1.6 | Tue | School Day | Off | Off | 22 | 19.96 | 2.04 | 1.7 | 3.8966 | 0.25 | 1035 | 1.7388 | 0
| 3:00 | 0.7 | Tue | School Day | Off | Off | 22 | 19.87 | 2.13 | 1.7 | 4.0685 | 0.25 | 1035 | 1.8155 | 0
| 4:00 | -0.8 | Tue | School Day | Off | Off | 22 | 19.72 | 2.28 | 1.7 | 4.355 | 0.25 | 1035 | 1.9434 | 0
| 5:00 | 1.3 | Tue | School Day | Off | Off | 22 | 19.93 | 2.07 | 1.7 | 3.9539 | 0.25 | 1035 | 1.7644 | 0
| 6:00 | 0.1 | Tue | School Day | Off | Off | 22 | 19.81 | 2.19 | 1.7 | 4.1831 | 0.25 | 1035 | 1.8667 | 0
| 7:00 | 0.7 | Tue | School Day | On | On | 22 | 19.87 | 2.13 | 1.7 | 4.0685 | 0.25 | 1035 | 1.8155 | 5.8841
| 8:00 | 0.9 | Tue | School Day | On | On | 22 | 19.89 | 2.11 | 1.7 | 4.0303 | 0.25 | 1035 | 1.7985 | 5.8288
| 9:00 | 0.9 | Tue | School Day | On | On | 22 | 19.89 | 2.11 | 1.7 | 4.0303 | 0.25 | 1035 | 1.7985 | 5.8288
| 10:00 | 2 | Tue | School Day | On | On | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 5.5249
| 11:00 | 2.9 | Tue | School Day | On | On | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 5.2763
| 12:00 | 5.8 | Tue | School Day | On | On | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 4.4752
| 13:00 | 7.4 | Tue | School Day | On | On | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 4.0332
| 14:00 | 8.6 | Tue | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 15:00 | 9.2 | Tue | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 16:00 | 9.2 | Tue | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 17:00 | 8.8 | Tue | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 18:00 | 8.9 | Tue | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 19:00 | 8.4 | Tue | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 20:00 | 8.6 | Tue | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 21:00 | 9.3 | Tue | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 22:00 | 9.7 | Tue | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 23:00 | 9.9 | Tue | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
Wed, 12/Jan | 24:00 | 9.9 | Wed | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 1:00 | 10 | Wed | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 2:00 | 9.9 | Wed | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 3:00 | 9.7 | Wed | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 4:00 | 9.7 | Wed | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 5:00 | 9.8 | Wed | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 6:00 | 10.2 | Wed | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 7:00 | 10.2 | Wed | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 8:00 | 10.4 | Wed | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 9:00 | 10.3 | Wed | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 10:00 | 10.4 | Wed | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 11:00 | 10.3 | Wed | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 12:00 | 9.6 | Wed | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 13:00 | 9.6 | Wed | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 14:00 | 8.9 | Wed | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 15:00 | 10.1 | Wed | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 16:00 | 9.6 | Wed | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 17:00 | 8.6 | Wed | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 18:00 | 6.6 | Wed | School Day | On | On | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 4.2542
| 19:00 | 6.1 | Wed | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 20:00 | 5 | Wed | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 21:00 | 3.8 | Wed | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 22:00 | 3.5 | Wed | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 23:00 | 3.4 | Wed | School Day | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
Thu, 13/Jan | 24:00 | 4.8 | Thu | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 1:00 | 3.6 | Thu | School Day | Off | Off | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 2:00 | 3.8 | Thu | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 3:00 | 3.6 | Thu | School Day | Off | Off | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 4:00 | 3.4 | Thu | School Day | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 5:00 | 2.5 | Thu | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 6:00 | 2.8 | Thu | School Day | Off | Off | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 7:00 | 2.6 | Thu | School Day | On | On | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 5.3592
| 8:00 | 4.4 | Thu | School Day | On | On | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 4.8619
| 9:00 | 4.5 | Thu | School Day | On | On | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 4.8343
| 10:00 | 6 | Thu | School Day | On | On | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 4.4199
| 11:00 | 8.1 | Thu | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 12:00 | 9.7 | Thu | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 13:00 | 10.3 | Thu | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 14:00 | 11 | Thu | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 15:00 | 10.9 | Thu | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 16:00 | 11 | Thu | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 17:00 | 11.4 | Thu | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 18:00 | 11.3 | Thu | School Day | On | On | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 2.9558
| 19:00 | 12 | Thu | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 20:00 | 12 | Thu | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 21:00 | 12.3 | Thu | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 22:00 | 12.2 | Thu | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 23:00 | 12.4 | Thu | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
Fri, 14/Jan | 24:00 | 12.6 | Fri | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 1:00 | 12.5 | Fri | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 2:00 | 12.2 | Fri | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 3:00 | 12.8 | Fri | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 4:00 | 13.1 | Fri | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 5:00 | 10.4 | Fri | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 6:00 | 9.6 | Fri | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 7:00 | 9.3 | Fri | School Day | On | On | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 3.5083
| 8:00 | 8.3 | Fri | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 9:00 | 7.6 | Fri | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 10:00 | 7 | Fri | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 11:00 | 8 | Fri | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 12:00 | 8.7 | Fri | School Day | On | On | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 3.6741
| 13:00 | 9.7 | Fri | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 14:00 | 10.2 | Fri | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 15:00 | 10.5 | Fri | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 16:00 | 10.4 | Fri | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 17:00 | 9.7 | Fri | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 18:00 | 8.7 | Fri | School Day | On | On | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 3.6741
| 19:00 | 8.3 | Fri | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 20:00 | 8 | Fri | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 21:00 | 8 | Fri | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 22:00 | 7.8 | Fri | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 23:00 | 7.8 | Fri | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
Sat, 15/Jan | 24:00 | 7.9 | Sat | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 1:00 | 7.8 | Sat | WE | Off | OFF | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 2:00 | 8 | Sat | WE | Off | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 3:00 | 8 | Sat | WE | Off | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 4:00 | 8.2 | Sat | WE | Off | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 5:00 | 8 | Sat | WE | Off | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 6:00 | 8.1 | Sat | WE | Off | OFF | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 7:00 | 8.1 | Sat | WE | On | OFF | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 8:00 | 8.4 | Sat | WE | On | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 9:00 | 8.6 | Sat | WE | On | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 10:00 | 9 | Sat | WE | On | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 11:00 | 9.7 | Sat | WE | On | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 12:00 | 10.3 | Sat | WE | On | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 13:00 | 10.8 | Sat | WE | On | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 14:00 | 11.1 | Sat | WE | On | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 15:00 | 11.5 | Sat | WE | On | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 16:00 | 11.6 | Sat | WE | On | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 17:00 | 11.7 | Sat | WE | On | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 18:00 | 11.4 | Sat | WE | On | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 19:00 | 11.3 | Sat | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 20:00 | 11.1 | Sat | WE | Off | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 21:00 | 10.9 | Sat | WE | Off | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 22:00 | 10.7 | Sat | WE | Off | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 23:00 | 10.5 | Sat | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
Sun, 16/Jan | 24:00 | 10.5 | Sun | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 1:00 | 10.3 | Sun | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 2:00 | 10.3 | Sun | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 3:00 | 10.3 | Sun | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 4:00 | 10.1 | Sun | WE | Off | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 5:00 | 9.9 | Sun | WE | Off | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 6:00 | 10.1 | Sun | WE | Off | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 7:00 | 10.1 | Sun | WE | On | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 8:00 | 10 | Sun | WE | On | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 9:00 | 10.1 | Sun | WE | On | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 10:00 | 10 | Sun | WE | On | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 11:00 | 10.1 | Sun | WE | On | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 12:00 | 10.3 | Sun | WE | On | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 13:00 | 10.7 | Sun | WE | On | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 14:00 | 10.8 | Sun | WE | On | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 15:00 | 10.7 | Sun | WE | On | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 16:00 | 10.3 | Sun | WE | On | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 17:00 | 9.9 | Sun | WE | On | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 18:00 | 9 | Sun | WE | On | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 19:00 | 9.1 | Sun | WE | Off | OFF | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 20:00 | 9 | Sun | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 21:00 | 9.4 | Sun | WE | Off | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 22:00 | 9.6 | Sun | WE | Off | OFF | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 23:00 | 9.7 | Sun | WE | Off | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
Mon, 17/Jan | 24:00 | 9.8 | Mon | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 1:00 | 10.3 | Mon | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 2:00 | 10.3 | Mon | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 3:00 | 10.6 | Mon | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 4:00 | 10.2 | Mon | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 5:00 | 10.3 | Mon | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 6:00 | 10.4 | Mon | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 7:00 | 10.2 | Mon | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 8:00 | 10.3 | Mon | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 9:00 | 10.2 | Mon | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 10:00 | 10.3 | Mon | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 11:00 | 10.5 | Mon | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 12:00 | 9.2 | Mon | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 13:00 | 8.3 | Mon | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 14:00 | 8.7 | Mon | School Day | On | On | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 3.6741
| 15:00 | 9.3 | Mon | School Day | On | On | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 3.5083
| 16:00 | 9.4 | Mon | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 17:00 | 9.1 | Mon | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 18:00 | 8.3 | Mon | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 19:00 | 7.6 | Mon | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 20:00 | 6.8 | Mon | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 21:00 | 5.9 | Mon | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 22:00 | 5 | Mon | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 23:00 | 4 | Mon | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
Tue, 18/Jan | 24:00 | 3.1 | Tue | School Day | Off | Off | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 1:00 | 2.5 | Tue | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 2:00 | 1.9 | Tue | School Day | Off | Off | 22 | 19.99 | 2.01 | 1.7 | 3.8393 | 0.25 | 1035 | 1.7133 | 0
| 3:00 | 1.2 | Tue | School Day | Off | Off | 22 | 19.92 | 2.08 | 1.7 | 3.973 | 0.25 | 1035 | 1.7729 | 0
| 4:00 | 1 | Tue | School Day | Off | Off | 22 | 19.9 | 2.1 | 1.7 | 4.0112 | 0.25 | 1035 | 1.79 | 0
| 5:00 | 0.4 | Tue | School Day | Off | Off | 22 | 19.84 | 2.16 | 1.7 | 4.1258 | 0.25 | 1035 | 1.8411 | 0
| 6:00 | 0.5 | Tue | School Day | Off | Off | 22 | 19.85 | 2.15 | 1.7 | 4.1067 | 0.25 | 1035 | 1.8326 | 0
| 7:00 | 0.4 | Tue | School Day | On | On | 22 | 19.84 | 2.16 | 1.7 | 4.1258 | 0.25 | 1035 | 1.8411 | 5.9669
| 8:00 | 0.5 | Tue | School Day | On | On | 22 | 19.85 | 2.15 | 1.7 | 4.1067 | 0.25 | 1035 | 1.8326 | 5.9393
| 9:00 | -0.1 | Tue | School Day | On | On | 22 | 19.79 | 2.21 | 1.7 | 4.2213 | 0.25 | 1035 | 1.8837 | 6.1051
| 10:00 | 0.7 | Tue | School Day | On | On | 22 | 19.87 | 2.13 | 1.7 | 4.0685 | 0.25 | 1035 | 1.8155 | 5.8841
| 11:00 | 1.5 | Tue | School Day | On | On | 22 | 19.95 | 2.05 | 1.7 | 3.9157 | 0.25 | 1035 | 1.7473 | 5.6631
| 12:00 | 3.1 | Tue | School Day | On | On | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 5.2211
| 13:00 | 4.8 | Tue | School Day | On | On | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 4.7514
| 14:00 | 7.1 | Tue | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 15:00 | 8 | Tue | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 16:00 | 7.9 | Tue | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 17:00 | 7 | Tue | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 18:00 | 6.5 | Tue | School Day | On | On | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 4.2818
| 19:00 | 5.1 | Tue | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 20:00 | 4.8 | Tue | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 21:00 | 4 | Tue | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 22:00 | 3.5 | Tue | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 23:00 | 2.5 | Tue | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
Wed, 19/Jan | 24:00 | 2.1 | Wed | School Day | Off | Off | 22 | 20.01 | 1.99 | 1.7 | 3.8011 | 0.25 | 1035 | 1.6962 | 0
| 1:00 | 0.5 | Wed | School Day | Off | Off | 22 | 19.85 | 2.15 | 1.7 | 4.1067 | 0.25 | 1035 | 1.8326 | 0
| 2:00 | -1.5 | Wed | School Day | Off | Off | 22 | 19.65 | 2.35 | 1.7 | 4.4887 | 0.25 | 1035 | 2.0031 | 0
| 3:00 | -3.3 | Wed | School Day | Off | Off | 22 | 19.47 | 2.53 | 1.7 | 4.8326 | 0.25 | 1035 | 2.1565 | 0
| 4:00 | -2.6 | Wed | School Day | Off | Off | 22 | 19.54 | 2.46 | 1.7 | 4.6989 | 0.25 | 1035 | 2.0968 | 0
| 5:00 | -1.7 | Wed | School Day | Off | Off | 22 | 19.63 | 2.37 | 1.7 | 4.5269 | 0.25 | 1035 | 2.0201 | 0
| 6:00 | -1.1 | Wed | School Day | Off | Off | 22 | 19.69 | 2.31 | 1.7 | 4.4123 | 0.25 | 1035 | 1.969 | 0
| 7:00 | -0.9 | Wed | School Day | On | On | 22 | 19.71 | 2.29 | 1.7 | 4.3741 | 0.25 | 1035 | 1.9519 | 6.3261
| 8:00 | -0.9 | Wed | School Day | On | On | 22 | 19.71 | 2.29 | 1.7 | 4.3741 | 0.25 | 1035 | 1.9519 | 6.3261
| 9:00 | -0.9 | Wed | School Day | On | On | 22 | 19.71 | 2.29 | 1.7 | 4.3741 | 0.25 | 1035 | 1.9519 | 6.3261
| 10:00 | -0.9 | Wed | School Day | On | On | 22 | 19.71 | 2.29 | 1.7 | 4.3741 | 0.25 | 1035 | 1.9519 | 6.3261
| 11:00 | 0 | Wed | School Day | On | On | 22 | 19.8 | 2.2 | 1.7 | 4.2022 | 0.25 | 1035 | 1.8752 | 6.0774
| 12:00 | 0.5 | Wed | School Day | On | On | 22 | 19.85 | 2.15 | 1.7 | 4.1067 | 0.25 | 1035 | 1.8326 | 5.9393
| 13:00 | 1 | Wed | School Day | On | On | 22 | 19.9 | 2.1 | 1.7 | 4.0112 | 0.25 | 1035 | 1.79 | 5.8012
| 14:00 | 2 | Wed | School Day | On | On | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 5.5249
| 15:00 | 2.6 | Wed | School Day | On | On | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 5.3592
| 16:00 | 3.1 | Wed | School Day | On | On | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 5.2211
| 17:00 | 3.6 | Wed | School Day | On | On | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 5.0829
| 18:00 | 4.2 | Wed | School Day | On | On | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 4.9172
| 19:00 | 4 | Wed | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 20:00 | 2.9 | Wed | School Day | Off | Off | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 21:00 | 4.4 | Wed | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 22:00 | 5.4 | Wed | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 23:00 | 4.3 | Wed | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
Thu, 20/Jan | 24:00 | 3.5 | Thu | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 1:00 | 3.8 | Thu | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 2:00 | 2.2 | Thu | School Day | Off | Off | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 0
| 3:00 | 1.5 | Thu | School Day | Off | Off | 22 | 19.95 | 2.05 | 1.7 | 3.9157 | 0.25 | 1035 | 1.7473 | 0
| 4:00 | 1.5 | Thu | School Day | Off | Off | 22 | 19.95 | 2.05 | 1.7 | 3.9157 | 0.25 | 1035 | 1.7473 | 0
| 5:00 | 1.6 | Thu | School Day | Off | Off | 22 | 19.96 | 2.04 | 1.7 | 3.8966 | 0.25 | 1035 | 1.7388 | 0
| 6:00 | 1.7 | Thu | School Day | Off | Off | 22 | 19.97 | 2.03 | 1.7 | 3.8775 | 0.25 | 1035 | 1.7303 | 0
| 7:00 | 1.9 | Thu | School Day | On | On | 22 | 19.99 | 2.01 | 1.7 | 3.8393 | 0.25 | 1035 | 1.7133 | 5.5526
| 8:00 | 2.9 | Thu | School Day | On | On | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 5.2763
| 9:00 | 3.7 | Thu | School Day | On | On | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 5.0553
| 10:00 | 4.4 | Thu | School Day | On | On | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 4.8619
| 11:00 | 5.1 | Thu | School Day | On | On | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 4.6686
| 12:00 | 6 | Thu | School Day | On | On | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 4.4199
| 13:00 | 7.1 | Thu | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 14:00 | 7.2 | Thu | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 15:00 | 7.4 | Thu | School Day | On | On | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 4.0332
| 16:00 | 7.4 | Thu | School Day | On | On | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 4.0332
| 17:00 | 7.4 | Thu | School Day | On | On | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 4.0332
| 18:00 | 7.5 | Thu | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 19:00 | 7.5 | Thu | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 20:00 | 7.3 | Thu | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 21:00 | 7.1 | Thu | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 22:00 | 6.5 | Thu | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 23:00 | 6.6 | Thu | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
Fri, 21/Jan | 24:00 | 6.7 | Fri | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 1:00 | 6.7 | Fri | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 2:00 | 7 | Fri | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 3:00 | 7.3 | Fri | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 4:00 | 7.3 | Fri | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 5:00 | 7.7 | Fri | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 6:00 | 8.1 | Fri | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 7:00 | 8 | Fri | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 8:00 | 8 | Fri | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 9:00 | 8.5 | Fri | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 10:00 | 9 | Fri | School Day | On | On | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 3.5912
| 11:00 | 8.9 | Fri | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 12:00 | 9.5 | Fri | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 13:00 | 10.1 | Fri | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 14:00 | 10.4 | Fri | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 15:00 | 9.3 | Fri | School Day | On | On | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 3.5083
| 16:00 | 8.4 | Fri | School Day | On | On | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 3.757
| 17:00 | 8.2 | Fri | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 18:00 | 6.3 | Fri | School Day | On | On | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 4.3371
| 19:00 | 6.2 | Fri | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 20:00 | 6 | Fri | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 21:00 | 5.5 | Fri | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 22:00 | 5.1 | Fri | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 23:00 | 4.8 | Fri | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
Sat, 22/Jan | 24:00 | 5.4 | Sat | WE | Off | OFF | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 1:00 | 5.3 | Sat | WE | Off | OFF | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 2:00 | 5.6 | Sat | WE | Off | OFF | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 3:00 | 5.8 | Sat | WE | Off | OFF | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 4:00 | 5.9 | Sat | WE | Off | OFF | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 5:00 | 5 | Sat | WE | Off | OFF | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 6:00 | 4 | Sat | WE | Off | OFF | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 7:00 | 3.6 | Sat | WE | On | OFF | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 8:00 | 2.9 | Sat | WE | On | OFF | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 9:00 | 2.4 | Sat | WE | On | OFF | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 10:00 | 2.3 | Sat | WE | On | OFF | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 0
| 11:00 | 4.2 | Sat | WE | On | OFF | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 12:00 | 6.4 | Sat | WE | On | OFF | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 13:00 | 7.9 | Sat | WE | On | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 14:00 | 9.2 | Sat | WE | On | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 15:00 | 9.8 | Sat | WE | On | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 16:00 | 10.1 | Sat | WE | On | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 17:00 | 8.9 | Sat | WE | On | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 18:00 | 7.8 | Sat | WE | On | OFF | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 19:00 | 7.4 | Sat | WE | Off | OFF | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 20:00 | 6.8 | Sat | WE | Off | OFF | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 21:00 | 6 | Sat | WE | Off | OFF | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 22:00 | 5.8 | Sat | WE | Off | OFF | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 23:00 | 5 | Sat | WE | Off | OFF | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
Sun, 23/Jan | 24:00 | 5 | Sun | WE | Off | OFF | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 1:00 | 4.6 | Sun | WE | Off | OFF | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 2:00 | 4 | Sun | WE | Off | OFF | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 3:00 | 4.1 | Sun | WE | Off | OFF | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 4:00 | 3.9 | Sun | WE | Off | OFF | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 5:00 | 4.9 | Sun | WE | Off | OFF | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 6:00 | 4.7 | Sun | WE | Off | OFF | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 7:00 | 4.5 | Sun | WE | On | OFF | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 8:00 | 5.3 | Sun | WE | On | OFF | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 9:00 | 6.7 | Sun | WE | On | OFF | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 10:00 | 8 | Sun | WE | On | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 11:00 | 8.9 | Sun | WE | On | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 12:00 | 10.5 | Sun | WE | On | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 13:00 | 11.3 | Sun | WE | On | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 14:00 | 11.5 | Sun | WE | On | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 15:00 | 11.7 | Sun | WE | On | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 16:00 | 11.3 | Sun | WE | On | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 17:00 | 10.9 | Sun | WE | On | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 18:00 | 10.9 | Sun | WE | On | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 19:00 | 9.7 | Sun | WE | Off | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 20:00 | 9.7 | Sun | WE | Off | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 21:00 | 9.5 | Sun | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 22:00 | 9.5 | Sun | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 23:00 | 9.5 | Sun | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
Mon, 24/Jan | 24:00 | 9.5 | Mon | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 1:00 | 9.5 | Mon | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 2:00 | 9.1 | Mon | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 3:00 | 8.8 | Mon | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 4:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 5:00 | 8.2 | Mon | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 6:00 | 7.8 | Mon | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 7:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 8:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 9:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 10:00 | 7.8 | Mon | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 11:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 12:00 | 8.2 | Mon | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 13:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 14:00 | 8.3 | Mon | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 15:00 | 8.3 | Mon | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 16:00 | 7.2 | Mon | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 17:00 | 6.3 | Mon | School Day | On | On | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 4.3371
| 18:00 | 6 | Mon | School Day | On | On | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 4.4199
| 19:00 | 5.6 | Mon | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 20:00 | 5.3 | Mon | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 21:00 | 5.1 | Mon | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 22:00 | 4.6 | Mon | School Day | Off | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 23:00 | 4.3 | Mon | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
Tue, 25/Jan | 24:00 | 4 | Tue | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 1:00 | 4.1 | Tue | School Day | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 2:00 | 4 | Tue | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 3:00 | 4.1 | Tue | School Day | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 4:00 | 4 | Tue | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 5:00 | 4 | Tue | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 6:00 | 3.9 | Tue | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 7:00 | 3.9 | Tue | School Day | On | On | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 5.0001
| 8:00 | 3.8 | Tue | School Day | On | On | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 5.0277
| 9:00 | 3.9 | Tue | School Day | On | On | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 5.0001
| 10:00 | 4.1 | Tue | School Day | On | On | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 4.9448
| 11:00 | 4.1 | Tue | School Day | On | On | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 4.9448
| 12:00 | 4.3 | Tue | School Day | On | On | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 4.8896
| 13:00 | 4.8 | Tue | School Day | On | On | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 4.7514
| 14:00 | 5.4 | Tue | School Day | On | On | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 4.5857
| 15:00 | 5.3 | Tue | School Day | On | On | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 4.6133
| 16:00 | 5.5 | Tue | School Day | On | On | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 4.5581
| 17:00 | 5.3 | Tue | School Day | On | On | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 4.6133
| 18:00 | 4.9 | Tue | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 19:00 | 4.9 | Tue | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 20:00 | 5 | Tue | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 21:00 | 5.5 | Tue | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 22:00 | 5.9 | Tue | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 23:00 | 5.8 | Tue | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
Wed, 26/Jan | 24:00 | 6 | Wed | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 1:00 | 5.8 | Wed | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 2:00 | 5.9 | Wed | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 3:00 | 4.8 | Wed | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 4:00 | 4.5 | Wed | School Day | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 5:00 | 4.3 | Wed | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 6:00 | 5.3 | Wed | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 7:00 | 4.9 | Wed | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 8:00 | 4.9 | Wed | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 9:00 | 5.1 | Wed | School Day | On | On | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 4.6686
| 10:00 | 6.6 | Wed | School Day | On | On | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 4.2542
| 11:00 | 7.7 | Wed | School Day | On | On | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 3.9503
| 12:00 | 9.2 | Wed | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 13:00 | 10.2 | Wed | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 14:00 | 10.5 | Wed | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 15:00 | 11 | Wed | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 16:00 | 11.5 | Wed | School Day | On | On | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 2.9006
| 17:00 | 11.4 | Wed | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 18:00 | 9.8 | Wed | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 19:00 | 9.1 | Wed | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 20:00 | 8 | Wed | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 21:00 | 8 | Wed | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 22:00 | 8.7 | Wed | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 23:00 | 7.4 | Wed | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
Thu, 27/Jan | 24:00 | 6.6 | Thu | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 1:00 | 7.1 | Thu | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 2:00 | 6.6 | Thu | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 3:00 | 7.4 | Thu | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 4:00 | 8.3 | Thu | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 5:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 6:00 | 8.6 | Thu | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 7:00 | 8.9 | Thu | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 8:00 | 8 | Thu | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 9:00 | 8.6 | Thu | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 10:00 | 8.6 | Thu | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 11:00 | 9.5 | Thu | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 12:00 | 10.6 | Thu | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 13:00 | 11.2 | Thu | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 14:00 | 11.8 | Thu | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 15:00 | 12.1 | Thu | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 16:00 | 12.2 | Thu | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 17:00 | 11.8 | Thu | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 18:00 | 11.6 | Thu | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 19:00 | 11.3 | Thu | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 20:00 | 11.1 | Thu | School Day | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 21:00 | 11 | Thu | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 22:00 | 10.7 | Thu | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 23:00 | 10.3 | Thu | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
Fri, 28/Jan | 24:00 | 9.5 | Fri | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 1:00 | 9.3 | Fri | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 2:00 | 9.2 | Fri | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 3:00 | 8.8 | Fri | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 4:00 | 8.4 | Fri | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 5:00 | 8.3 | Fri | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 6:00 | 8.7 | Fri | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 7:00 | 9.4 | Fri | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 8:00 | 9.8 | Fri | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 9:00 | 10.1 | Fri | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 10:00 | 10.4 | Fri | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 11:00 | 10.6 | Fri | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 12:00 | 10.8 | Fri | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 13:00 | 10.8 | Fri | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 14:00 | 8 | Fri | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 15:00 | 7.6 | Fri | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 16:00 | 7.3 | Fri | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 17:00 | 7.2 | Fri | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 18:00 | 6.9 | Fri | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 19:00 | 6.9 | Fri | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 20:00 | 6.4 | Fri | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 21:00 | 5.4 | Fri | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 22:00 | 4.6 | Fri | School Day | Off | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 23:00 | 3.7 | Fri | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
Sat, 29/Jan | 24:00 | 2.8 | Sat | WE | Off | OFF | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 1:00 | 1.9 | Sat | WE | Off | OFF | 22 | 19.99 | 2.01 | 1.7 | 3.8393 | 0.25 | 1035 | 1.7133 | 0
| 2:00 | 0.9 | Sat | WE | Off | OFF | 22 | 19.89 | 2.11 | 1.7 | 4.0303 | 0.25 | 1035 | 1.7985 | 0
| 3:00 | 0.8 | Sat | WE | Off | OFF | 22 | 19.88 | 2.12 | 1.7 | 4.0494 | 0.25 | 1035 | 1.807 | 0
| 4:00 | 0.1 | Sat | WE | Off | OFF | 22 | 19.81 | 2.19 | 1.7 | 4.1831 | 0.25 | 1035 | 1.8667 | 0
| 5:00 | 0 | Sat | WE | Off | OFF | 22 | 19.8 | 2.2 | 1.7 | 4.2022 | 0.25 | 1035 | 1.8752 | 0
| 6:00 | 0.3 | Sat | WE | Off | OFF | 22 | 19.83 | 2.17 | 1.7 | 4.1449 | 0.25 | 1035 | 1.8496 | 0
| 7:00 | -0.1 | Sat | WE | On | OFF | 22 | 19.79 | 2.21 | 1.7 | 4.2213 | 0.25 | 1035 | 1.8837 | 0
| 8:00 | -0.3 | Sat | WE | On | OFF | 22 | 19.77 | 2.23 | 1.7 | 4.2595 | 0.25 | 1035 | 1.9008 | 0
| 9:00 | -0.4 | Sat | WE | On | OFF | 22 | 19.76 | 2.24 | 1.7 | 4.2786 | 0.25 | 1035 | 1.9093 | 0
| 10:00 | -0.3 | Sat | WE | On | OFF | 22 | 19.77 | 2.23 | 1.7 | 4.2595 | 0.25 | 1035 | 1.9008 | 0
| 11:00 | 0 | Sat | WE | On | OFF | 22 | 19.8 | 2.2 | 1.7 | 4.2022 | 0.25 | 1035 | 1.8752 | 0
| 12:00 | 0.7 | Sat | WE | On | OFF | 22 | 19.87 | 2.13 | 1.7 | 4.0685 | 0.25 | 1035 | 1.8155 | 0
| 13:00 | 2.4 | Sat | WE | On | OFF | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 14:00 | 3.8 | Sat | WE | On | OFF | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 15:00 | 6 | Sat | WE | On | OFF | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 16:00 | 8.2 | Sat | WE | On | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 17:00 | 8 | Sat | WE | On | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 18:00 | 7.2 | Sat | WE | On | OFF | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 19:00 | 6.2 | Sat | WE | Off | OFF | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 20:00 | 6.1 | Sat | WE | Off | OFF | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 21:00 | 5.7 | Sat | WE | Off | OFF | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 22:00 | 5.2 | Sat | WE | Off | OFF | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 23:00 | 4.5 | Sat | WE | Off | OFF | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
Sun, 30/Jan | 24:00 | 3.3 | Sun | WE | Off | OFF | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 1:00 | 3.8 | Sun | WE | Off | OFF | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 2:00 | 3.6 | Sun | WE | Off | OFF | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 3:00 | 2.5 | Sun | WE | Off | OFF | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 4:00 | 1.6 | Sun | WE | Off | OFF | 22 | 19.96 | 2.04 | 1.7 | 3.8966 | 0.25 | 1035 | 1.7388 | 0
| 5:00 | 2.1 | Sun | WE | Off | OFF | 22 | 20.01 | 1.99 | 1.7 | 3.8011 | 0.25 | 1035 | 1.6962 | 0
| 6:00 | 1.7 | Sun | WE | Off | OFF | 22 | 19.97 | 2.03 | 1.7 | 3.8775 | 0.25 | 1035 | 1.7303 | 0
| 7:00 | 2.5 | Sun | WE | On | OFF | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 8:00 | 2.5 | Sun | WE | On | OFF | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 9:00 | 2.6 | Sun | WE | On | OFF | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 0
| 10:00 | 3.1 | Sun | WE | On | OFF | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 11:00 | 4.2 | Sun | WE | On | OFF | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 12:00 | 5.9 | Sun | WE | On | OFF | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 13:00 | 7.4 | Sun | WE | On | OFF | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 14:00 | 8.6 | Sun | WE | On | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 15:00 | 9.2 | Sun | WE | On | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 16:00 | 9.5 | Sun | WE | On | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 17:00 | 9.5 | Sun | WE | On | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 18:00 | 9.3 | Sun | WE | On | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 19:00 | 8.9 | Sun | WE | Off | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 20:00 | 9 | Sun | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 21:00 | 9 | Sun | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 22:00 | 8.4 | Sun | WE | Off | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 23:00 | 7.9 | Sun | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
Mon, 31/Jan | 24:00 | 7.8 | Mon | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 1:00 | 8.2 | Mon | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 2:00 | 8.3 | Mon | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 3:00 | 7.8 | Mon | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 4:00 | 7.8 | Mon | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 5:00 | 8.1 | Mon | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 6:00 | 7.9 | Mon | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 7:00 | 8.1 | Mon | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 8:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 9:00 | 7.8 | Mon | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 10:00 | 7.8 | Mon | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 11:00 | 7.8 | Mon | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 12:00 | 7.8 | Mon | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 13:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 14:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 15:00 | 8.2 | Mon | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 16:00 | 8.2 | Mon | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 17:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 18:00 | 6.6 | Mon | School Day | On | On | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 4.2542
| 19:00 | 5.2 | Mon | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 20:00 | 6.2 | Mon | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 21:00 | 6.2 | Mon | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 22:00 | 5 | Mon | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 23:00 | 2.8 | Mon | School Day | Off | Off | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
Tue, 01/Feb | 24:00 | 5.5 | Tue | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 1:00 | 5.4 | Tue | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 2:00 | 5.4 | Tue | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 3:00 | 4.3 | Tue | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 4:00 | 3.9 | Tue | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 5:00 | 3.6 | Tue | School Day | Off | Off | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 6:00 | 3.5 | Tue | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 7:00 | 3.8 | Tue | School Day | On | On | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 5.0277
| 8:00 | 4.2 | Tue | School Day | On | On | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 4.9172
| 9:00 | 4.4 | Tue | School Day | On | On | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 4.8619
| 10:00 | 4.5 | Tue | School Day | On | On | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 4.8343
| 11:00 | 4.7 | Tue | School Day | On | On | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 4.7791
| 12:00 | 4.7 | Tue | School Day | On | On | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 4.7791
| 13:00 | 4.9 | Tue | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 14:00 | 4.9 | Tue | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 15:00 | 5.1 | Tue | School Day | On | On | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 4.6686
| 16:00 | 5 | Tue | School Day | On | On | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 4.6962
| 17:00 | 5 | Tue | School Day | On | On | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 4.6962
| 18:00 | 5 | Tue | School Day | On | On | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 4.6962
| 19:00 | 4.8 | Tue | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 20:00 | 4.9 | Tue | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 21:00 | 4.3 | Tue | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 22:00 | 3.8 | Tue | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 23:00 | 3.1 | Tue | School Day | Off | Off | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
Wed, 02/Feb | 24:00 | 1.8 | Wed | School Day | Off | Off | 22 | 19.98 | 2.02 | 1.7 | 3.8584 | 0.25 | 1035 | 1.7218 | 0
| 1:00 | 2.3 | Wed | School Day | Off | Off | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 0
| 2:00 | 2 | Wed | School Day | Off | Off | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 0
| 3:00 | 1.4 | Wed | School Day | Off | Off | 22 | 19.94 | 2.06 | 1.7 | 3.9348 | 0.25 | 1035 | 1.7559 | 0
| 4:00 | 0.7 | Wed | School Day | Off | Off | 22 | 19.87 | 2.13 | 1.7 | 4.0685 | 0.25 | 1035 | 1.8155 | 0
| 5:00 | 0.4 | Wed | School Day | Off | Off | 22 | 19.84 | 2.16 | 1.7 | 4.1258 | 0.25 | 1035 | 1.8411 | 0
| 6:00 | 1.9 | Wed | School Day | Off | Off | 22 | 19.99 | 2.01 | 1.7 | 3.8393 | 0.25 | 1035 | 1.7133 | 0
| 7:00 | 2.2 | Wed | School Day | On | On | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 5.4697
| 8:00 | 2.5 | Wed | School Day | On | On | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 5.3868
| 9:00 | 2.6 | Wed | School Day | On | On | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 5.3592
| 10:00 | 2.6 | Wed | School Day | On | On | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 5.3592
| 11:00 | 2.9 | Wed | School Day | On | On | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 5.2763
| 12:00 | 3.7 | Wed | School Day | On | On | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 5.0553
| 13:00 | 3.8 | Wed | School Day | On | On | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 5.0277
| 14:00 | 4.2 | Wed | School Day | On | On | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 4.9172
| 15:00 | 5.9 | Wed | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 16:00 | 6.4 | Wed | School Day | On | On | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 4.3095
| 17:00 | 6 | Wed | School Day | On | On | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 4.4199
| 18:00 | 5.8 | Wed | School Day | On | On | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 4.4752
| 19:00 | 6.2 | Wed | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 20:00 | 6 | Wed | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 21:00 | 5.2 | Wed | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 22:00 | 5 | Wed | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 23:00 | 4.4 | Wed | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
Thu, 03/Feb | 24:00 | 3.9 | Thu | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 1:00 | 4.4 | Thu | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 2:00 | 4.8 | Thu | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 3:00 | 4.5 | Thu | School Day | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 4:00 | 3.9 | Thu | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 5:00 | 3.8 | Thu | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 6:00 | 3.3 | Thu | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 7:00 | 3.3 | Thu | School Day | On | On | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 5.1658
| 8:00 | 1.9 | Thu | School Day | On | On | 22 | 19.99 | 2.01 | 1.7 | 3.8393 | 0.25 | 1035 | 1.7133 | 5.5526
| 9:00 | 3.1 | Thu | School Day | On | On | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 5.2211
| 10:00 | 3.1 | Thu | School Day | On | On | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 5.2211
| 11:00 | 4.7 | Thu | School Day | On | On | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 4.7791
| 12:00 | 7.6 | Thu | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 13:00 | 9.1 | Thu | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 14:00 | 10.9 | Thu | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 15:00 | 11 | Thu | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 16:00 | 11.1 | Thu | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 17:00 | 10.5 | Thu | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 18:00 | 10.3 | Thu | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 19:00 | 9.1 | Thu | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 20:00 | 8.4 | Thu | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 21:00 | 8 | Thu | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 22:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 23:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
Fri, 04/Feb | 24:00 | 7.8 | Fri | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 1:00 | 8 | Fri | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 2:00 | 8.2 | Fri | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 3:00 | 7.9 | Fri | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 4:00 | 8.1 | Fri | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 5:00 | 8.2 | Fri | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 6:00 | 8.5 | Fri | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 7:00 | 8.5 | Fri | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 8:00 | 8.8 | Fri | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 9:00 | 9.1 | Fri | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 10:00 | 9.5 | Fri | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 11:00 | 10.2 | Fri | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 12:00 | 10.8 | Fri | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 13:00 | 11.4 | Fri | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 14:00 | 11.6 | Fri | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 15:00 | 11.8 | Fri | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 16:00 | 11.6 | Fri | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 17:00 | 11.7 | Fri | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 18:00 | 11.5 | Fri | School Day | On | On | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 2.9006
| 19:00 | 11.5 | Fri | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 20:00 | 11.3 | Fri | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 21:00 | 11.8 | Fri | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 22:00 | 11.9 | Fri | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 23:00 | 11.8 | Fri | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
Sat, 05/Feb | 24:00 | 12.2 | Sat | WE | Off | OFF | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 1:00 | 12.5 | Sat | WE | Off | OFF | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 2:00 | 11.9 | Sat | WE | Off | OFF | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 3:00 | 11.4 | Sat | WE | Off | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 4:00 | 10.8 | Sat | WE | Off | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 5:00 | 10.1 | Sat | WE | Off | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 6:00 | 10.1 | Sat | WE | Off | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 7:00 | 9.5 | Sat | WE | On | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 8:00 | 10 | Sat | WE | On | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 9:00 | 9.9 | Sat | WE | On | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 10:00 | 9.9 | Sat | WE | On | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 11:00 | 10.5 | Sat | WE | On | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 12:00 | 10.9 | Sat | WE | On | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 13:00 | 12 | Sat | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 14:00 | 12.5 | Sat | WE | On | OFF | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 15:00 | 12.4 | Sat | WE | On | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 16:00 | 12.5 | Sat | WE | On | OFF | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 17:00 | 12.4 | Sat | WE | On | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 18:00 | 12.4 | Sat | WE | On | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 19:00 | 11.9 | Sat | WE | Off | OFF | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 20:00 | 11.6 | Sat | WE | Off | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 21:00 | 11 | Sat | WE | Off | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 22:00 | 11.5 | Sat | WE | Off | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 23:00 | 11.2 | Sat | WE | Off | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
Sun, 06/Feb | 24:00 | 11.2 | Sun | WE | Off | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 1:00 | 11.6 | Sun | WE | Off | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 2:00 | 11.7 | Sun | WE | Off | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 3:00 | 11.6 | Sun | WE | Off | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 4:00 | 11.6 | Sun | WE | Off | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 5:00 | 10.6 | Sun | WE | Off | OFF | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 6:00 | 10.3 | Sun | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 7:00 | 10.3 | Sun | WE | On | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 8:00 | 10.3 | Sun | WE | On | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 9:00 | 11.1 | Sun | WE | On | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 10:00 | 11.9 | Sun | WE | On | OFF | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 11:00 | 13.4 | Sun | WE | On | OFF | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 12:00 | 14.8 | Sun | WE | On | OFF | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 13:00 | 15.4 | Sun | WE | On | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 14:00 | 15.8 | Sun | WE | On | OFF | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 15:00 | 15.5 | Sun | WE | On | OFF | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 16:00 | 15.1 | Sun | WE | On | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 17:00 | 14.6 | Sun | WE | On | OFF | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 18:00 | 13.2 | Sun | WE | On | OFF | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 19:00 | 12.6 | Sun | WE | Off | OFF | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 20:00 | 11.8 | Sun | WE | Off | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 21:00 | 11.2 | Sun | WE | Off | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 22:00 | 11.3 | Sun | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 23:00 | 11.5 | Sun | WE | Off | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
Mon, 07/Feb | 24:00 | 11.6 | Mon | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 1:00 | 11.4 | Mon | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 2:00 | 11.6 | Mon | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 3:00 | 11.5 | Mon | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 4:00 | 11.6 | Mon | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 5:00 | 10.9 | Mon | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 6:00 | 10.5 | Mon | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 7:00 | 9.9 | Mon | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 8:00 | 9.7 | Mon | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 9:00 | 9.9 | Mon | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 10:00 | 10.1 | Mon | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 11:00 | 10.5 | Mon | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 12:00 | 11.5 | Mon | School Day | On | On | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 2.9006
| 13:00 | 12.4 | Mon | School Day | On | On | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 2.652
| 14:00 | 12.2 | Mon | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 15:00 | 12.7 | Mon | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 16:00 | 13 | Mon | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 17:00 | 12.7 | Mon | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 18:00 | 11.6 | Mon | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 19:00 | 10.2 | Mon | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 20:00 | 9.5 | Mon | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 21:00 | 9.4 | Mon | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 22:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 23:00 | 8.4 | Mon | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
Tue, 08/Feb | 24:00 | 7.6 | Tue | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 1:00 | 6.2 | Tue | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 2:00 | 6.5 | Tue | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 3:00 | 6.8 | Tue | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 4:00 | 6.5 | Tue | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 5:00 | 6.3 | Tue | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 6:00 | 6.9 | Tue | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 7:00 | 7.1 | Tue | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 8:00 | 6.3 | Tue | School Day | On | On | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 4.3371
| 9:00 | 5.6 | Tue | School Day | On | On | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 4.5304
| 10:00 | 7.3 | Tue | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 11:00 | 7.9 | Tue | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 12:00 | 9.1 | Tue | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 13:00 | 11.1 | Tue | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 14:00 | 12.1 | Tue | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 15:00 | 12.9 | Tue | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 16:00 | 12.4 | Tue | School Day | On | On | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 2.652
| 17:00 | 11.9 | Tue | School Day | On | On | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 2.7901
| 18:00 | 10.9 | Tue | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 19:00 | 9 | Tue | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 20:00 | 7.5 | Tue | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 21:00 | 6.6 | Tue | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 22:00 | 6.9 | Tue | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 23:00 | 5.8 | Tue | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
Wed, 09/Feb | 24:00 | 6.5 | Wed | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 1:00 | 5.2 | Wed | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 2:00 | 4.6 | Wed | School Day | Off | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 3:00 | 5.1 | Wed | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 4:00 | 5.3 | Wed | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 5:00 | 4.4 | Wed | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 6:00 | 6.2 | Wed | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 7:00 | 6.5 | Wed | School Day | On | On | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 4.2818
| 8:00 | 4.9 | Wed | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 9:00 | 3.6 | Wed | School Day | On | On | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 5.0829
| 10:00 | 4.9 | Wed | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 11:00 | 7.1 | Wed | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 12:00 | 8.7 | Wed | School Day | On | On | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 3.6741
| 13:00 | 10.3 | Wed | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 14:00 | 11.6 | Wed | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 15:00 | 12.4 | Wed | School Day | On | On | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 2.652
| 16:00 | 12.5 | Wed | School Day | On | On | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 2.6243
| 17:00 | 12.5 | Wed | School Day | On | On | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 2.6243
| 18:00 | 10.9 | Wed | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 19:00 | 9.7 | Wed | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 20:00 | 8.9 | Wed | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 21:00 | 8.6 | Wed | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 22:00 | 8.8 | Wed | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 23:00 | 8.2 | Wed | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
Thu, 10/Feb | 24:00 | 8.4 | Thu | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 1:00 | 8.3 | Thu | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 2:00 | 7.1 | Thu | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 3:00 | 6.6 | Thu | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 4:00 | 6.7 | Thu | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 5:00 | 6.6 | Thu | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 6:00 | 5.9 | Thu | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 7:00 | 6.7 | Thu | School Day | On | On | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 4.2266
| 8:00 | 5.7 | Thu | School Day | On | On | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 4.5028
| 9:00 | 7.3 | Thu | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 10:00 | 9.2 | Thu | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 11:00 | 10.4 | Thu | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 12:00 | 9 | Thu | School Day | On | On | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 3.5912
| 13:00 | 9.9 | Thu | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 14:00 | 9.9 | Thu | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 15:00 | 10.3 | Thu | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 16:00 | 9.9 | Thu | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 17:00 | 9.8 | Thu | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 18:00 | 9.4 | Thu | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 19:00 | 8.5 | Thu | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 20:00 | 6.9 | Thu | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 21:00 | 6.3 | Thu | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 22:00 | 4.8 | Thu | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 23:00 | 4.9 | Thu | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
Fri, 11/Feb | 24:00 | 2.9 | Fri | School Day | Off | Off | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 1:00 | 2.8 | Fri | School Day | Off | Off | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 2:00 | 2.4 | Fri | School Day | Off | Off | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 3:00 | 1 | Fri | School Day | Off | Off | 22 | 19.9 | 2.1 | 1.7 | 4.0112 | 0.25 | 1035 | 1.79 | 0
| 4:00 | 1.1 | Fri | School Day | Off | Off | 22 | 19.91 | 2.09 | 1.7 | 3.9921 | 0.25 | 1035 | 1.7814 | 0
| 5:00 | 0.8 | Fri | School Day | Off | Off | 22 | 19.88 | 2.12 | 1.7 | 4.0494 | 0.25 | 1035 | 1.807 | 0
| 6:00 | -0.1 | Fri | School Day | Off | Off | 22 | 19.79 | 2.21 | 1.7 | 4.2213 | 0.25 | 1035 | 1.8837 | 0
| 7:00 | -0.5 | Fri | School Day | On | On | 22 | 19.75 | 2.25 | 1.7 | 4.2977 | 0.25 | 1035 | 1.9178 | 6.2156
| 8:00 | -0.8 | Fri | School Day | On | On | 22 | 19.72 | 2.28 | 1.7 | 4.355 | 0.25 | 1035 | 1.9434 | 6.2984
| 9:00 | 0.2 | Fri | School Day | On | On | 22 | 19.82 | 2.18 | 1.7 | 4.164 | 0.25 | 1035 | 1.8582 | 6.0222
| 10:00 | 2.2 | Fri | School Day | On | On | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 5.4697
| 11:00 | 4.9 | Fri | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 12:00 | 8.2 | Fri | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 13:00 | 10.2 | Fri | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 14:00 | 10.7 | Fri | School Day | On | On | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 3.1216
| 15:00 | 10.9 | Fri | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 16:00 | 11.4 | Fri | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 17:00 | 11.1 | Fri | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 18:00 | 10.6 | Fri | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 19:00 | 10.2 | Fri | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 20:00 | 9.7 | Fri | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 21:00 | 9.6 | Fri | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 22:00 | 9.6 | Fri | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 23:00 | 9.2 | Fri | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
Sat, 12/Feb | 24:00 | 9.3 | Sat | WE | Off | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 1:00 | 9.8 | Sat | WE | Off | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 2:00 | 10 | Sat | WE | Off | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 3:00 | 9.9 | Sat | WE | Off | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 4:00 | 9.5 | Sat | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 5:00 | 9.4 | Sat | WE | Off | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 6:00 | 9.7 | Sat | WE | Off | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 7:00 | 9.9 | Sat | WE | On | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 8:00 | 8.6 | Sat | WE | On | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 9:00 | 8.2 | Sat | WE | On | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 10:00 | 8.7 | Sat | WE | On | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 11:00 | 8.8 | Sat | WE | On | OFF | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 12:00 | 9.2 | Sat | WE | On | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 13:00 | 10.2 | Sat | WE | On | OFF | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 14:00 | 11.1 | Sat | WE | On | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 15:00 | 11.7 | Sat | WE | On | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 16:00 | 11.6 | Sat | WE | On | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 17:00 | 11.7 | Sat | WE | On | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 18:00 | 11 | Sat | WE | On | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 19:00 | 10.1 | Sat | WE | Off | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 20:00 | 9 | Sat | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 21:00 | 8 | Sat | WE | Off | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 22:00 | 4.8 | Sat | WE | Off | OFF | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 23:00 | 5.3 | Sat | WE | Off | OFF | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
Sun, 13/Feb | 24:00 | 5.8 | Sun | WE | Off | OFF | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 1:00 | 4.8 | Sun | WE | Off | OFF | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 2:00 | 3.5 | Sun | WE | Off | OFF | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 3:00 | 3.4 | Sun | WE | Off | OFF | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 4:00 | 3.1 | Sun | WE | Off | OFF | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 5:00 | 3.1 | Sun | WE | Off | OFF | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 6:00 | 2.2 | Sun | WE | Off | OFF | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 0
| 7:00 | 4.1 | Sun | WE | On | OFF | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 8:00 | 3.9 | Sun | WE | On | OFF | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 9:00 | 5.2 | Sun | WE | On | OFF | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 10:00 | 6.8 | Sun | WE | On | OFF | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 11:00 | 8.3 | Sun | WE | On | OFF | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 12:00 | 9.8 | Sun | WE | On | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 13:00 | 10.2 | Sun | WE | On | OFF | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 14:00 | 10.2 | Sun | WE | On | OFF | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 15:00 | 10.1 | Sun | WE | On | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 16:00 | 10.5 | Sun | WE | On | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 17:00 | 11.3 | Sun | WE | On | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 18:00 | 11.4 | Sun | WE | On | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 19:00 | 11.5 | Sun | WE | Off | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 20:00 | 11.2 | Sun | WE | Off | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 21:00 | 10.7 | Sun | WE | Off | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 22:00 | 8.7 | Sun | WE | Off | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 23:00 | 8.6 | Sun | WE | Off | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
Mon, 14/Feb | 24:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 1:00 | 6.9 | Mon | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 2:00 | 5.7 | Mon | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 3:00 | 5.6 | Mon | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 4:00 | 5.4 | Mon | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 5:00 | 5.8 | Mon | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 6:00 | 6 | Mon | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 7:00 | 5.7 | Mon | School Day | On | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 8:00 | 5.8 | Mon | School Day | On | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 9:00 | 4.9 | Mon | School Day | On | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 10:00 | 6.2 | Mon | School Day | On | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 11:00 | 7.7 | Mon | School Day | On | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 12:00 | 9 | Mon | School Day | On | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 13:00 | 9.8 | Mon | School Day | On | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 14:00 | 10.2 | Mon | School Day | On | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 15:00 | 9.9 | Mon | School Day | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 16:00 | 9.9 | Mon | School Day | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 17:00 | 9.2 | Mon | School Day | On | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 18:00 | 8.6 | Mon | School Day | On | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 19:00 | 8.2 | Mon | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 20:00 | 8.3 | Mon | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 21:00 | 8.4 | Mon | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 22:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 23:00 | 8.5 | Mon | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
Tue, 15/Feb | 24:00 | 8.3 | Tue | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 1:00 | 8.5 | Tue | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 2:00 | 9 | Tue | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 3:00 | 9.4 | Tue | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 4:00 | 9.5 | Tue | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 5:00 | 9.8 | Tue | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 6:00 | 9.8 | Tue | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 7:00 | 9.7 | Tue | School Day | On | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 8:00 | 9.9 | Tue | School Day | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 9:00 | 10.6 | Tue | School Day | On | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 10:00 | 10.3 | Tue | School Day | On | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 11:00 | 10.9 | Tue | School Day | On | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 12:00 | 11.4 | Tue | School Day | On | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 13:00 | 11.9 | Tue | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 14:00 | 12.1 | Tue | School Day | On | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 15:00 | 11.8 | Tue | School Day | On | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 16:00 | 9.8 | Tue | School Day | On | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 17:00 | 9 | Tue | School Day | On | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 18:00 | 9.1 | Tue | School Day | On | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 19:00 | 7.9 | Tue | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 20:00 | 6.5 | Tue | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 21:00 | 6.1 | Tue | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 22:00 | 4.6 | Tue | School Day | Off | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 23:00 | 3.7 | Tue | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
Wed, 16/Feb | 24:00 | 2.5 | Wed | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 1:00 | 2.5 | Wed | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 2:00 | 2 | Wed | School Day | Off | Off | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 0
| 3:00 | 1.2 | Wed | School Day | Off | Off | 22 | 19.92 | 2.08 | 1.7 | 3.973 | 0.25 | 1035 | 1.7729 | 0
| 4:00 | 0.6 | Wed | School Day | Off | Off | 22 | 19.86 | 2.14 | 1.7 | 4.0876 | 0.25 | 1035 | 1.8241 | 0
| 5:00 | 0.4 | Wed | School Day | Off | Off | 22 | 19.84 | 2.16 | 1.7 | 4.1258 | 0.25 | 1035 | 1.8411 | 0
| 6:00 | -0.1 | Wed | School Day | Off | Off | 22 | 19.79 | 2.21 | 1.7 | 4.2213 | 0.25 | 1035 | 1.8837 | 0
| 7:00 | 0.4 | Wed | School Day | On | Off | 22 | 19.84 | 2.16 | 1.7 | 4.1258 | 0.25 | 1035 | 1.8411 | 0
| 8:00 | 0.7 | Wed | School Day | On | Off | 22 | 19.87 | 2.13 | 1.7 | 4.0685 | 0.25 | 1035 | 1.8155 | 0
| 9:00 | 1.7 | Wed | School Day | On | Off | 22 | 19.97 | 2.03 | 1.7 | 3.8775 | 0.25 | 1035 | 1.7303 | 0
| 10:00 | 2.9 | Wed | School Day | On | Off | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 11:00 | 5 | Wed | School Day | On | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 12:00 | 6.9 | Wed | School Day | On | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 13:00 | 7.4 | Wed | School Day | On | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 14:00 | 8.3 | Wed | School Day | On | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 15:00 | 7.8 | Wed | School Day | On | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 16:00 | 8 | Wed | School Day | On | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 17:00 | 8.6 | Wed | School Day | On | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 18:00 | 7.3 | Wed | School Day | On | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 19:00 | 5.3 | Wed | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 20:00 | 5.2 | Wed | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 21:00 | 5.2 | Wed | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 22:00 | 3.7 | Wed | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 23:00 | 3.4 | Wed | School Day | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
Thu, 17/Feb | 24:00 | 2.2 | Thu | School Day | Off | Off | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 0
| 1:00 | 1.6 | Thu | School Day | Off | Off | 22 | 19.96 | 2.04 | 1.7 | 3.8966 | 0.25 | 1035 | 1.7388 | 0
| 2:00 | 1.2 | Thu | School Day | Off | Off | 22 | 19.92 | 2.08 | 1.7 | 3.973 | 0.25 | 1035 | 1.7729 | 0
| 3:00 | 1.1 | Thu | School Day | Off | Off | 22 | 19.91 | 2.09 | 1.7 | 3.9921 | 0.25 | 1035 | 1.7814 | 0
| 4:00 | 2.5 | Thu | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 5:00 | 3.4 | Thu | School Day | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 6:00 | 4.2 | Thu | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 7:00 | 4.3 | Thu | School Day | On | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 8:00 | 4 | Thu | School Day | On | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 9:00 | 4.3 | Thu | School Day | On | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 10:00 | 5.1 | Thu | School Day | On | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 11:00 | 5.9 | Thu | School Day | On | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 12:00 | 6.8 | Thu | School Day | On | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 13:00 | 8.2 | Thu | School Day | On | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 14:00 | 9.2 | Thu | School Day | On | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 15:00 | 9.9 | Thu | School Day | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 16:00 | 11.2 | Thu | School Day | On | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 17:00 | 11.6 | Thu | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 18:00 | 11.9 | Thu | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 19:00 | 11.3 | Thu | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 20:00 | 10.5 | Thu | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 21:00 | 9.8 | Thu | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 22:00 | 9.7 | Thu | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 23:00 | 9.7 | Thu | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
Fri, 18/Feb | 24:00 | 10.2 | Fri | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 1:00 | 10.9 | Fri | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 2:00 | 11 | Fri | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 3:00 | 11.4 | Fri | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 4:00 | 11.7 | Fri | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 5:00 | 12 | Fri | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 6:00 | 11.9 | Fri | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 7:00 | 12 | Fri | School Day | On | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 8:00 | 12.4 | Fri | School Day | On | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 9:00 | 13.1 | Fri | School Day | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 10:00 | 13.4 | Fri | School Day | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 11:00 | 13.5 | Fri | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 12:00 | 14 | Fri | School Day | On | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 13:00 | 14.1 | Fri | School Day | On | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 14:00 | 14.1 | Fri | School Day | On | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 15:00 | 13.9 | Fri | School Day | On | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 16:00 | 13.9 | Fri | School Day | On | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 17:00 | 13.9 | Fri | School Day | On | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 18:00 | 14 | Fri | School Day | On | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 19:00 | 14 | Fri | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 20:00 | 13.6 | Fri | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 21:00 | 13.6 | Fri | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 22:00 | 13.7 | Fri | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 23:00 | 13.4 | Fri | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
Sat, 19/Feb | 24:00 | 12.7 | Sat | WE | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 1:00 | 13 | Sat | WE | Off | OFF | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 2:00 | 13.4 | Sat | WE | Off | OFF | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 3:00 | 13.7 | Sat | WE | Off | OFF | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 4:00 | 13.2 | Sat | WE | Off | OFF | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 5:00 | 13.3 | Sat | WE | Off | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 6:00 | 13.1 | Sat | WE | Off | OFF | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 7:00 | 12.4 | Sat | WE | On | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 8:00 | 12.4 | Sat | WE | On | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 9:00 | 12.1 | Sat | WE | On | OFF | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 10:00 | 11.8 | Sat | WE | On | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 11:00 | 12.3 | Sat | WE | On | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 12:00 | 12.8 | Sat | WE | On | OFF | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 13:00 | 13.6 | Sat | WE | On | OFF | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 14:00 | 13.6 | Sat | WE | On | OFF | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 15:00 | 13.9 | Sat | WE | On | OFF | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 16:00 | 13.3 | Sat | WE | On | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 17:00 | 12.9 | Sat | WE | On | OFF | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 18:00 | 12.4 | Sat | WE | On | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 19:00 | 11.8 | Sat | WE | Off | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 20:00 | 11.1 | Sat | WE | Off | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 21:00 | 10.9 | Sat | WE | Off | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 22:00 | 10.8 | Sat | WE | Off | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 23:00 | 8.7 | Sat | WE | Off | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
Sun, 20/Feb | 24:00 | 8.6 | Sun | WE | Off | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 1:00 | 8.9 | Sun | WE | Off | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 2:00 | 9.3 | Sun | WE | Off | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 3:00 | 9.2 | Sun | WE | Off | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 4:00 | 9.2 | Sun | WE | Off | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 5:00 | 8.7 | Sun | WE | Off | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 6:00 | 8.3 | Sun | WE | Off | OFF | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 7:00 | 7.6 | Sun | WE | On | OFF | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 8:00 | 7 | Sun | WE | On | OFF | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 9:00 | 6.8 | Sun | WE | On | OFF | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 10:00 | 7.6 | Sun | WE | On | OFF | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 11:00 | 8.6 | Sun | WE | On | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 12:00 | 9.8 | Sun | WE | On | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 13:00 | 10.6 | Sun | WE | On | OFF | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 14:00 | 11 | Sun | WE | On | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 15:00 | 11.3 | Sun | WE | On | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 16:00 | 11.2 | Sun | WE | On | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 17:00 | 9.9 | Sun | WE | On | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 18:00 | 9.5 | Sun | WE | On | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 19:00 | 7.8 | Sun | WE | Off | OFF | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 20:00 | 7.2 | Sun | WE | Off | OFF | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 21:00 | 6.7 | Sun | WE | Off | OFF | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 22:00 | 5.6 | Sun | WE | Off | OFF | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 23:00 | 4.9 | Sun | WE | Off | OFF | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
Mon, 21/Feb | 24:00 | 5.6 | Mon | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 1:00 | 5.3 | Mon | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 2:00 | 4.3 | Mon | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 3:00 | 4.5 | Mon | School Day | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 4:00 | 4.3 | Mon | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 5:00 | 4 | Mon | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 6:00 | 4 | Mon | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 7:00 | 3.8 | Mon | School Day | On | On | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 5.0277
| 8:00 | 2.4 | Mon | School Day | On | On | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 5.4144
| 9:00 | 2.5 | Mon | School Day | On | On | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 5.3868
| 10:00 | 4.9 | Mon | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 11:00 | 7 | Mon | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 12:00 | 9.7 | Mon | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 13:00 | 10.1 | Mon | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 14:00 | 11.2 | Mon | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 15:00 | 11.3 | Mon | School Day | On | On | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 2.9558
| 16:00 | 11.4 | Mon | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 17:00 | 10.9 | Mon | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 18:00 | 9.6 | Mon | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 19:00 | 9 | Mon | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 20:00 | 8.2 | Mon | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 21:00 | 7.3 | Mon | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 22:00 | 6.9 | Mon | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 23:00 | 6.4 | Mon | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
Tue, 22/Feb | 24:00 | 5.7 | Tue | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 1:00 | 6 | Tue | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 2:00 | 5.3 | Tue | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 3:00 | 5.2 | Tue | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 4:00 | 6.7 | Tue | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 5:00 | 6.7 | Tue | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 6:00 | 6.9 | Tue | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 7:00 | 7.3 | Tue | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 8:00 | 7.9 | Tue | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 9:00 | 7.8 | Tue | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 10:00 | 8.1 | Tue | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 11:00 | 8 | Tue | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 12:00 | 8.5 | Tue | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 13:00 | 7.7 | Tue | School Day | On | On | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 3.9503
| 14:00 | 8.2 | Tue | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 15:00 | 9.2 | Tue | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 16:00 | 10.1 | Tue | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 17:00 | 7 | Tue | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 18:00 | 7.5 | Tue | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 19:00 | 7.1 | Tue | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 20:00 | 5.9 | Tue | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 21:00 | 4.9 | Tue | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 22:00 | 4.9 | Tue | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 23:00 | 3.5 | Tue | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
Wed, 23/Feb | 24:00 | 3.7 | Wed | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 1:00 | 3.5 | Wed | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 2:00 | 3.2 | Wed | School Day | Off | Off | 22 | 20.12 | 1.88 | 1.7 | 3.591 | 0.25 | 1035 | 1.6024 | 0
| 3:00 | 2.5 | Wed | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 4:00 | 2.4 | Wed | School Day | Off | Off | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 5:00 | 1.2 | Wed | School Day | Off | Off | 22 | 19.92 | 2.08 | 1.7 | 3.973 | 0.25 | 1035 | 1.7729 | 0
| 6:00 | 1.8 | Wed | School Day | Off | Off | 22 | 19.98 | 2.02 | 1.7 | 3.8584 | 0.25 | 1035 | 1.7218 | 0
| 7:00 | 2 | Wed | School Day | On | On | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 5.5249
| 8:00 | 1.4 | Wed | School Day | On | On | 22 | 19.94 | 2.06 | 1.7 | 3.9348 | 0.25 | 1035 | 1.7559 | 5.6907
| 9:00 | 2.3 | Wed | School Day | On | On | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 5.4421
| 10:00 | 3.5 | Wed | School Day | On | On | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 5.1106
| 11:00 | 5.4 | Wed | School Day | On | On | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 4.5857
| 12:00 | 6.9 | Wed | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 13:00 | 8.3 | Wed | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 14:00 | 8 | Wed | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 15:00 | 8.8 | Wed | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 16:00 | 7.9 | Wed | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 17:00 | 8.3 | Wed | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 18:00 | 7.5 | Wed | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 19:00 | 6.4 | Wed | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 20:00 | 5.8 | Wed | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 21:00 | 5.5 | Wed | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 22:00 | 5.5 | Wed | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 23:00 | 5.8 | Wed | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
Thu, 24/Feb | 24:00 | 5.6 | Thu | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 1:00 | 5.7 | Thu | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 2:00 | 4.4 | Thu | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 3:00 | 5.5 | Thu | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 4:00 | 5.8 | Thu | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 5:00 | 5.6 | Thu | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 6:00 | 6.1 | Thu | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 7:00 | 5.9 | Thu | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 8:00 | 6.2 | Thu | School Day | On | On | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 4.3647
| 9:00 | 6.9 | Thu | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 10:00 | 6.8 | Thu | School Day | On | On | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 4.199
| 11:00 | 6.8 | Thu | School Day | On | On | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 4.199
| 12:00 | 5.9 | Thu | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 13:00 | 5.4 | Thu | School Day | On | On | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 4.5857
| 14:00 | 5.5 | Thu | School Day | On | On | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 4.5581
| 15:00 | 6 | Thu | School Day | On | On | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 4.4199
| 16:00 | 5.9 | Thu | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 17:00 | 6.4 | Thu | School Day | On | On | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 4.3095
| 18:00 | 5.9 | Thu | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 19:00 | 5.9 | Thu | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 20:00 | 5.5 | Thu | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 21:00 | 5.7 | Thu | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 22:00 | 5.8 | Thu | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 23:00 | 4.9 | Thu | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
Fri, 25/Feb | 24:00 | 3.5 | Fri | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 1:00 | 5 | Fri | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 2:00 | 5 | Fri | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 3:00 | 3.8 | Fri | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 4:00 | 3.6 | Fri | School Day | Off | Off | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 5:00 | 3.1 | Fri | School Day | Off | Off | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 6:00 | 3 | Fri | School Day | Off | Off | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 7:00 | 3 | Fri | School Day | On | On | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 5.2487
| 8:00 | 2.6 | Fri | School Day | On | On | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 5.3592
| 9:00 | 3.7 | Fri | School Day | On | On | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 5.0553
| 10:00 | 4.8 | Fri | School Day | On | On | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 4.7514
| 11:00 | 4.6 | Fri | School Day | On | On | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 4.8067
| 12:00 | 5.7 | Fri | School Day | On | On | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 4.5028
| 13:00 | 6 | Fri | School Day | On | On | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 4.4199
| 14:00 | 6.8 | Fri | School Day | On | On | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 4.199
| 15:00 | 6.4 | Fri | School Day | On | On | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 4.3095
| 16:00 | 5.9 | Fri | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 17:00 | 5.4 | Fri | School Day | On | On | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 4.5857
| 18:00 | 5.1 | Fri | School Day | On | On | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 4.6686
| 19:00 | 5 | Fri | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 20:00 | 4.9 | Fri | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 21:00 | 4.8 | Fri | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 22:00 | 4.2 | Fri | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 23:00 | 3.8 | Fri | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
Sat, 26/Feb | 24:00 | 3.5 | Sat | WE | Off | OFF | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 1:00 | 2.4 | Sat | WE | Off | OFF | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 2:00 | 3 | Sat | WE | Off | OFF | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 3:00 | 3.4 | Sat | WE | Off | OFF | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 4:00 | 4.1 | Sat | WE | Off | OFF | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 5:00 | 4 | Sat | WE | Off | OFF | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 6:00 | 3.7 | Sat | WE | Off | OFF | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 7:00 | 2.9 | Sat | WE | On | OFF | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 8:00 | 3.5 | Sat | WE | On | OFF | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 9:00 | 3.4 | Sat | WE | On | OFF | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 10:00 | 4.9 | Sat | WE | On | OFF | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 11:00 | 6.1 | Sat | WE | On | OFF | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 12:00 | 8.1 | Sat | WE | On | OFF | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 13:00 | 7.7 | Sat | WE | On | OFF | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 14:00 | 8.9 | Sat | WE | On | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 15:00 | 8.8 | Sat | WE | On | OFF | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 16:00 | 7.7 | Sat | WE | On | OFF | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 17:00 | 7.8 | Sat | WE | On | OFF | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 18:00 | 7.9 | Sat | WE | On | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 19:00 | 7.6 | Sat | WE | Off | OFF | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 20:00 | 5 | Sat | WE | Off | OFF | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 21:00 | 5.1 | Sat | WE | Off | OFF | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 22:00 | 4.2 | Sat | WE | Off | OFF | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 23:00 | 3.1 | Sat | WE | Off | OFF | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
Sun, 27/Feb | 24:00 | 2.5 | Sun | WE | Off | OFF | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 1:00 | 2.9 | Sun | WE | Off | OFF | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 2:00 | 3 | Sun | WE | Off | OFF | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 3:00 | 2.8 | Sun | WE | Off | OFF | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 4:00 | 3.4 | Sun | WE | Off | OFF | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 5:00 | 3.6 | Sun | WE | Off | OFF | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 6:00 | 2.9 | Sun | WE | Off | OFF | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 7:00 | 2.2 | Sun | WE | On | OFF | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 0
| 8:00 | 3 | Sun | WE | On | OFF | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 9:00 | 4.4 | Sun | WE | On | OFF | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 10:00 | 5.7 | Sun | WE | On | OFF | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 11:00 | 6.8 | Sun | WE | On | OFF | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 12:00 | 8.9 | Sun | WE | On | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 13:00 | 9.3 | Sun | WE | On | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 14:00 | 9.5 | Sun | WE | On | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 15:00 | 10 | Sun | WE | On | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 16:00 | 9.8 | Sun | WE | On | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 17:00 | 9.6 | Sun | WE | On | OFF | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 18:00 | 8 | Sun | WE | On | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 19:00 | 7.8 | Sun | WE | Off | OFF | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 20:00 | 7.2 | Sun | WE | Off | OFF | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 21:00 | 5.3 | Sun | WE | Off | OFF | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 22:00 | 3.5 | Sun | WE | Off | OFF | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 23:00 | 3.3 | Sun | WE | Off | OFF | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
Mon, 28/Feb | 24:00 | 2.7 | Mon | School Day | Off | Off | 22 | 20.07 | 1.93 | 1.7 | 3.6865 | 0.25 | 1035 | 1.6451 | 0
| 1:00 | 2.9 | Mon | School Day | Off | Off | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 2:00 | 2.7 | Mon | School Day | Off | Off | 22 | 20.07 | 1.93 | 1.7 | 3.6865 | 0.25 | 1035 | 1.6451 | 0
| 3:00 | 2.3 | Mon | School Day | Off | Off | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 0
| 4:00 | 2.3 | Mon | School Day | Off | Off | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 0
| 5:00 | 2.1 | Mon | School Day | Off | Off | 22 | 20.01 | 1.99 | 1.7 | 3.8011 | 0.25 | 1035 | 1.6962 | 0
| 6:00 | 2.2 | Mon | School Day | Off | Off | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 0
| 7:00 | 1.8 | Mon | School Day | On | On | 22 | 19.98 | 2.02 | 1.7 | 3.8584 | 0.25 | 1035 | 1.7218 | 5.5802
| 8:00 | 1.8 | Mon | School Day | On | On | 22 | 19.98 | 2.02 | 1.7 | 3.8584 | 0.25 | 1035 | 1.7218 | 5.5802
| 9:00 | 2.6 | Mon | School Day | On | On | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 5.3592
| 10:00 | 4.6 | Mon | School Day | On | On | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 4.8067
| 11:00 | 6.4 | Mon | School Day | On | On | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 4.3095
| 12:00 | 7.6 | Mon | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 13:00 | 8.9 | Mon | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 14:00 | 9 | Mon | School Day | On | On | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 3.5912
| 15:00 | 10.3 | Mon | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 16:00 | 10 | Mon | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 17:00 | 9.9 | Mon | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 18:00 | 7.6 | Mon | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 19:00 | 6.7 | Mon | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 20:00 | 6.3 | Mon | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 21:00 | 6.2 | Mon | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 22:00 | 6.3 | Mon | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 23:00 | 6.2 | Mon | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
Tue, 01/Mar | 24:00 | 6.6 | Tue | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 1:00 | 5.8 | Tue | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 2:00 | 5.9 | Tue | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 3:00 | 6.4 | Tue | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 4:00 | 6.6 | Tue | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 5:00 | 6.7 | Tue | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 6:00 | 6.6 | Tue | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 7:00 | 6.5 | Tue | School Day | On | On | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 4.2818
| 8:00 | 6.3 | Tue | School Day | On | On | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 4.3371
| 9:00 | 6.4 | Tue | School Day | On | On | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 4.3095
| 10:00 | 7.2 | Tue | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 11:00 | 8.1 | Tue | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 12:00 | 8.8 | Tue | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 13:00 | 9.8 | Tue | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 14:00 | 9.5 | Tue | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 15:00 | 9.6 | Tue | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 16:00 | 9.6 | Tue | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 17:00 | 9.6 | Tue | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 18:00 | 9.4 | Tue | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 19:00 | 8.5 | Tue | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 20:00 | 8 | Tue | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 21:00 | 7.9 | Tue | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 22:00 | 6.3 | Tue | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 23:00 | 6.5 | Tue | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
Wed, 02/Mar | 24:00 | 5.9 | Wed | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 1:00 | 5.3 | Wed | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 2:00 | 4.3 | Wed | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 3:00 | 3.3 | Wed | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 4:00 | 3.9 | Wed | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 5:00 | 4.8 | Wed | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 6:00 | 4.1 | Wed | School Day | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 7:00 | 4.1 | Wed | School Day | On | On | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 4.9448
| 8:00 | 4.7 | Wed | School Day | On | On | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 4.7791
| 9:00 | 5.9 | Wed | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 10:00 | 6.7 | Wed | School Day | On | On | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 4.2266
| 11:00 | 7.5 | Wed | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 12:00 | 7.2 | Wed | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 13:00 | 7.5 | Wed | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 14:00 | 8 | Wed | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 15:00 | 9.9 | Wed | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 16:00 | 13.2 | Wed | School Day | On | On | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 2.431
| 17:00 | 12.9 | Wed | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 18:00 | 12 | Wed | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 19:00 | 11.5 | Wed | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 20:00 | 10.5 | Wed | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 21:00 | 9.6 | Wed | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 22:00 | 9.6 | Wed | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 23:00 | 9.4 | Wed | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
Thu, 03/Mar | 24:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 1:00 | 7.2 | Thu | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 2:00 | 7.5 | Thu | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 3:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 4:00 | 7.4 | Thu | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 5:00 | 6.8 | Thu | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 6:00 | 7 | Thu | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 7:00 | 6.9 | Thu | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 8:00 | 7 | Thu | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 9:00 | 7.5 | Thu | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 10:00 | 8.3 | Thu | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 11:00 | 8.8 | Thu | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 12:00 | 9.6 | Thu | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 13:00 | 10.8 | Thu | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 14:00 | 10.9 | Thu | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 15:00 | 11.4 | Thu | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 16:00 | 11.1 | Thu | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 17:00 | 11.1 | Thu | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 18:00 | 12 | Thu | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 19:00 | 9.7 | Thu | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 20:00 | 10.8 | Thu | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 21:00 | 9.5 | Thu | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 22:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 23:00 | 7.7 | Thu | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
Fri, 04/Mar | 24:00 | 6 | Fri | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 1:00 | 4.9 | Fri | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 2:00 | 5.3 | Fri | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 3:00 | 5.1 | Fri | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 4:00 | 4.8 | Fri | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 5:00 | 4.8 | Fri | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 6:00 | 5.4 | Fri | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 7:00 | 5.9 | Fri | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 8:00 | 7.1 | Fri | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 9:00 | 8.7 | Fri | School Day | On | On | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 3.6741
| 10:00 | 9.2 | Fri | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 11:00 | 10.8 | Fri | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 12:00 | 11 | Fri | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 13:00 | 11 | Fri | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 14:00 | 11.1 | Fri | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 15:00 | 12.4 | Fri | School Day | On | On | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 2.652
| 16:00 | 13.3 | Fri | School Day | On | On | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 2.4033
| 17:00 | 13.9 | Fri | School Day | On | On | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 2.2376
| 18:00 | 13.4 | Fri | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 19:00 | 12 | Fri | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 20:00 | 11.8 | Fri | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 21:00 | 11.8 | Fri | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 22:00 | 11.9 | Fri | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 23:00 | 12 | Fri | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
Sat, 05/Mar | 24:00 | 11.6 | Sat | WE | Off | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 1:00 | 11.3 | Sat | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 2:00 | 11.6 | Sat | WE | Off | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 3:00 | 11.3 | Sat | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 4:00 | 11.3 | Sat | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 5:00 | 11.4 | Sat | WE | Off | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 6:00 | 11.3 | Sat | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 7:00 | 11.4 | Sat | WE | On | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 8:00 | 11.8 | Sat | WE | On | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 9:00 | 11.9 | Sat | WE | On | OFF | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 10:00 | 12.4 | Sat | WE | On | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 11:00 | 13.3 | Sat | WE | On | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 12:00 | 15.1 | Sat | WE | On | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 13:00 | 15.4 | Sat | WE | On | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 14:00 | 16.3 | Sat | WE | On | OFF | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 15:00 | 16.5 | Sat | WE | On | OFF | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 16:00 | 15.6 | Sat | WE | On | OFF | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 17:00 | 15.4 | Sat | WE | On | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 18:00 | 14.3 | Sat | WE | On | OFF | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 19:00 | 13.5 | Sat | WE | Off | OFF | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 20:00 | 12.3 | Sat | WE | Off | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 21:00 | 12.1 | Sat | WE | Off | OFF | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 22:00 | 11.7 | Sat | WE | Off | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 23:00 | 11.3 | Sat | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
Sun, 06/Mar | 24:00 | 10.4 | Sun | WE | Off | OFF | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 1:00 | 10.7 | Sun | WE | Off | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 2:00 | 11 | Sun | WE | Off | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 3:00 | 11.1 | Sun | WE | Off | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 4:00 | 11.2 | Sun | WE | Off | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 5:00 | 10.9 | Sun | WE | Off | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 6:00 | 9.8 | Sun | WE | Off | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 7:00 | 9.8 | Sun | WE | On | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 8:00 | 9.8 | Sun | WE | On | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 9:00 | 10.2 | Sun | WE | On | OFF | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 10:00 | 12.7 | Sun | WE | On | OFF | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 11:00 | 13.3 | Sun | WE | On | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 12:00 | 14.6 | Sun | WE | On | OFF | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 13:00 | 15.6 | Sun | WE | On | OFF | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 14:00 | 18.3 | Sun | WE | On | OFF | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 15:00 | 17.8 | Sun | WE | On | OFF | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 16:00 | 17.1 | Sun | WE | On | OFF | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 17:00 | 16.2 | Sun | WE | On | OFF | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 18:00 | 15.3 | Sun | WE | On | OFF | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 19:00 | 14.2 | Sun | WE | Off | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 20:00 | 13.9 | Sun | WE | Off | OFF | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 21:00 | 14.1 | Sun | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 22:00 | 13.9 | Sun | WE | Off | OFF | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 23:00 | 12.9 | Sun | WE | Off | OFF | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
Mon, 07/Mar | 24:00 | 12.7 | Mon | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 1:00 | 12.1 | Mon | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 2:00 | 10.6 | Mon | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 3:00 | 10.4 | Mon | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 4:00 | 9.8 | Mon | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 5:00 | 9.4 | Mon | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 6:00 | 8.9 | Mon | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 7:00 | 8.3 | Mon | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 8:00 | 8 | Mon | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 9:00 | 8.5 | Mon | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 10:00 | 9.1 | Mon | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 11:00 | 9.7 | Mon | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 12:00 | 9.6 | Mon | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 13:00 | 9.8 | Mon | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 14:00 | 10.1 | Mon | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 15:00 | 10.3 | Mon | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 16:00 | 10.3 | Mon | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 17:00 | 10.2 | Mon | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 18:00 | 9.9 | Mon | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 19:00 | 9.5 | Mon | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 20:00 | 8.2 | Mon | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 21:00 | 7.6 | Mon | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 22:00 | 6.8 | Mon | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 23:00 | 5.3 | Mon | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
Tue, 08/Mar | 24:00 | 5 | Tue | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 1:00 | 3.8 | Tue | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 2:00 | 3 | Tue | School Day | Off | Off | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 3:00 | 2.9 | Tue | School Day | Off | Off | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 4:00 | 1.8 | Tue | School Day | Off | Off | 22 | 19.98 | 2.02 | 1.7 | 3.8584 | 0.25 | 1035 | 1.7218 | 0
| 5:00 | 1.6 | Tue | School Day | Off | Off | 22 | 19.96 | 2.04 | 1.7 | 3.8966 | 0.25 | 1035 | 1.7388 | 0
| 6:00 | 1.4 | Tue | School Day | Off | Off | 22 | 19.94 | 2.06 | 1.7 | 3.9348 | 0.25 | 1035 | 1.7559 | 0
| 7:00 | 0.8 | Tue | School Day | On | On | 22 | 19.88 | 2.12 | 1.7 | 4.0494 | 0.25 | 1035 | 1.807 | 5.8564
| 8:00 | 0.6 | Tue | School Day | On | On | 22 | 19.86 | 2.14 | 1.7 | 4.0876 | 0.25 | 1035 | 1.8241 | 5.9117
| 9:00 | 2.2 | Tue | School Day | On | On | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 5.4697
| 10:00 | 4.6 | Tue | School Day | On | On | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 4.8067
| 11:00 | 7.2 | Tue | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 12:00 | 9.5 | Tue | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 13:00 | 10.4 | Tue | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 14:00 | 11 | Tue | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 15:00 | 11 | Tue | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 16:00 | 11 | Tue | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 17:00 | 10.6 | Tue | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 18:00 | 10.1 | Tue | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 19:00 | 8.9 | Tue | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 20:00 | 8.5 | Tue | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 21:00 | 8.2 | Tue | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 22:00 | 8.7 | Tue | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 23:00 | 9.2 | Tue | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
Wed, 09/Mar | 24:00 | 9.9 | Wed | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 1:00 | 9.6 | Wed | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 2:00 | 9.6 | Wed | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 3:00 | 9.6 | Wed | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 4:00 | 9.6 | Wed | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 5:00 | 9.8 | Wed | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 6:00 | 10 | Wed | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 7:00 | 10 | Wed | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 8:00 | 10.3 | Wed | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 9:00 | 10.6 | Wed | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 10:00 | 10.6 | Wed | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 11:00 | 10.3 | Wed | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 12:00 | 10.4 | Wed | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 13:00 | 10.4 | Wed | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 14:00 | 11.4 | Wed | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 15:00 | 11.4 | Wed | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 16:00 | 12 | Wed | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 17:00 | 12 | Wed | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 18:00 | 12.4 | Wed | School Day | On | On | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 2.652
| 19:00 | 11.7 | Wed | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 20:00 | 11.6 | Wed | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 21:00 | 12 | Wed | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 22:00 | 11.7 | Wed | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 23:00 | 11.5 | Wed | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
Thu, 10/Mar | 24:00 | 11.5 | Thu | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 1:00 | 11.7 | Thu | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 2:00 | 11.4 | Thu | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 3:00 | 11 | Thu | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 4:00 | 11.2 | Thu | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 5:00 | 11 | Thu | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 6:00 | 11.4 | Thu | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 7:00 | 10.2 | Thu | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 8:00 | 10.3 | Thu | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 9:00 | 10.8 | Thu | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 10:00 | 11.2 | Thu | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 11:00 | 11.2 | Thu | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 12:00 | 11.7 | Thu | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 13:00 | 12 | Thu | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 14:00 | 11.9 | Thu | School Day | On | On | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 2.7901
| 15:00 | 12.7 | Thu | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 16:00 | 12.5 | Thu | School Day | On | On | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 2.6243
| 17:00 | 12.5 | Thu | School Day | On | On | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 2.6243
| 18:00 | 12.2 | Thu | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 19:00 | 12.1 | Thu | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 20:00 | 11.5 | Thu | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 21:00 | 10.5 | Thu | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 22:00 | 9.9 | Thu | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 23:00 | 9.6 | Thu | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
Fri, 11/Mar | 24:00 | 9.2 | Fri | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 1:00 | 9.2 | Fri | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 2:00 | 9.2 | Fri | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 3:00 | 8.8 | Fri | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 4:00 | 8.9 | Fri | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 5:00 | 8.6 | Fri | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 6:00 | 8.4 | Fri | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 7:00 | 7.9 | Fri | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 8:00 | 8.3 | Fri | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 9:00 | 8.5 | Fri | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 10:00 | 9.4 | Fri | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 11:00 | 9.9 | Fri | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 12:00 | 10.9 | Fri | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 13:00 | 11.7 | Fri | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 14:00 | 12 | Fri | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 15:00 | 12.2 | Fri | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 16:00 | 12.1 | Fri | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 17:00 | 11.7 | Fri | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 18:00 | 10.5 | Fri | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 19:00 | 9.2 | Fri | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 20:00 | 9 | Fri | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 21:00 | 7.9 | Fri | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 22:00 | 8.2 | Fri | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 23:00 | 8.4 | Fri | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
Sat, 12/Mar | 24:00 | 6.5 | Sat | WE | Off | OFF | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 1:00 | 5.4 | Sat | WE | Off | OFF | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 2:00 | 5.2 | Sat | WE | Off | OFF | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 3:00 | 4.4 | Sat | WE | Off | OFF | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 4:00 | 3.8 | Sat | WE | Off | OFF | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 5:00 | 3.2 | Sat | WE | Off | OFF | 22 | 20.12 | 1.88 | 1.7 | 3.591 | 0.25 | 1035 | 1.6024 | 0
| 6:00 | 2.8 | Sat | WE | Off | OFF | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 7:00 | 3.5 | Sat | WE | On | OFF | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 8:00 | 2.9 | Sat | WE | On | OFF | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 9:00 | 3.9 | Sat | WE | On | OFF | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 10:00 | 6.5 | Sat | WE | On | OFF | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 11:00 | 7.6 | Sat | WE | On | OFF | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 12:00 | 8.6 | Sat | WE | On | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 13:00 | 9.5 | Sat | WE | On | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 14:00 | 9.8 | Sat | WE | On | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 15:00 | 11.1 | Sat | WE | On | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 16:00 | 11.2 | Sat | WE | On | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 17:00 | 11.1 | Sat | WE | On | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 18:00 | 10.8 | Sat | WE | On | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 19:00 | 11 | Sat | WE | Off | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 20:00 | 11.1 | Sat | WE | Off | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 21:00 | 11.3 | Sat | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 22:00 | 11.4 | Sat | WE | Off | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 23:00 | 10.7 | Sat | WE | Off | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
Sun, 13/Mar | 24:00 | 9.8 | Sun | WE | Off | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 1:00 | 9.3 | Sun | WE | Off | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 2:00 | 9.3 | Sun | WE | Off | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 3:00 | 9.3 | Sun | WE | Off | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 4:00 | 9 | Sun | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 5:00 | 8.9 | Sun | WE | Off | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 6:00 | 8.9 | Sun | WE | Off | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 7:00 | 8.7 | Sun | WE | On | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 8:00 | 8.3 | Sun | WE | On | OFF | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 9:00 | 8 | Sun | WE | On | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 10:00 | 9.1 | Sun | WE | On | OFF | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 11:00 | 10 | Sun | WE | On | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 12:00 | 10.8 | Sun | WE | On | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 13:00 | 11.4 | Sun | WE | On | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 14:00 | 12.2 | Sun | WE | On | OFF | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 15:00 | 12 | Sun | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 16:00 | 12.6 | Sun | WE | On | OFF | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 17:00 | 11.6 | Sun | WE | On | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 18:00 | 11.6 | Sun | WE | On | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 19:00 | 10.6 | Sun | WE | Off | OFF | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 20:00 | 8.8 | Sun | WE | Off | OFF | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 21:00 | 8.5 | Sun | WE | Off | OFF | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 22:00 | 7.8 | Sun | WE | Off | OFF | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 23:00 | 6.8 | Sun | WE | Off | OFF | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
Mon, 14/Mar | 24:00 | 6.8 | Mon | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 1:00 | 5.8 | Mon | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 2:00 | 5.7 | Mon | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 3:00 | 4.7 | Mon | School Day | Off | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 4:00 | 5.8 | Mon | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 5:00 | 5.7 | Mon | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 6:00 | 5.7 | Mon | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 7:00 | 5.9 | Mon | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 8:00 | 6 | Mon | School Day | On | On | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 4.4199
| 9:00 | 6.7 | Mon | School Day | On | On | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 4.2266
| 10:00 | 8.1 | Mon | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 11:00 | 9.2 | Mon | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 12:00 | 10.8 | Mon | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 13:00 | 10.4 | Mon | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 14:00 | 11.1 | Mon | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 15:00 | 10.9 | Mon | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 16:00 | 9.4 | Mon | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 17:00 | 8.9 | Mon | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 18:00 | 8.5 | Mon | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 19:00 | 7.8 | Mon | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 20:00 | 7.2 | Mon | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 21:00 | 7.8 | Mon | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 22:00 | 8.4 | Mon | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 23:00 | 9.1 | Mon | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
Tue, 15/Mar | 24:00 | 10.2 | Tue | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 1:00 | 11.3 | Tue | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 2:00 | 11.6 | Tue | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 3:00 | 11.8 | Tue | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 4:00 | 11.5 | Tue | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 5:00 | 11.5 | Tue | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 6:00 | 11.1 | Tue | School Day | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 7:00 | 11.2 | Tue | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 8:00 | 9.7 | Tue | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 9:00 | 9.2 | Tue | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 10:00 | 9.6 | Tue | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 11:00 | 10.3 | Tue | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 12:00 | 11.7 | Tue | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 13:00 | 11.9 | Tue | School Day | On | On | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 2.7901
| 14:00 | 12.5 | Tue | School Day | On | On | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 2.6243
| 15:00 | 11.6 | Tue | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 16:00 | 12.8 | Tue | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 17:00 | 12.6 | Tue | School Day | On | On | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 2.5967
| 18:00 | 11.1 | Tue | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 19:00 | 10 | Tue | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 20:00 | 10.2 | Tue | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 21:00 | 9.7 | Tue | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 22:00 | 9.5 | Tue | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 23:00 | 9.3 | Tue | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
Wed, 16/Mar | 24:00 | 8.5 | Wed | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 1:00 | 8.8 | Wed | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 2:00 | 8.5 | Wed | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 3:00 | 7.8 | Wed | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 4:00 | 7.9 | Wed | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 5:00 | 7.8 | Wed | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 6:00 | 7.6 | Wed | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 7:00 | 6.7 | Wed | School Day | On | On | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 4.2266
| 8:00 | 6.9 | Wed | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 9:00 | 6.9 | Wed | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 10:00 | 7.4 | Wed | School Day | On | On | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 4.0332
| 11:00 | 7.4 | Wed | School Day | On | On | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 4.0332
| 12:00 | 7.4 | Wed | School Day | On | On | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 4.0332
| 13:00 | 7.3 | Wed | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 14:00 | 7 | Wed | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 15:00 | 6.9 | Wed | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 16:00 | 6.3 | Wed | School Day | On | On | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 4.3371
| 17:00 | 5.7 | Wed | School Day | On | On | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 4.5028
| 18:00 | 5 | Wed | School Day | On | On | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 4.6962
| 19:00 | 4.1 | Wed | School Day | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 20:00 | 4.2 | Wed | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 21:00 | 4.4 | Wed | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 22:00 | 4.5 | Wed | School Day | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 23:00 | 4.2 | Wed | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
Thu, 17/Mar | 24:00 | 4.2 | Thu | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 1:00 | 4 | Thu | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 2:00 | 4.5 | Thu | School Day | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 3:00 | 4.3 | Thu | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 4:00 | 3.9 | Thu | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 5:00 | 4 | Thu | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 6:00 | 3.8 | Thu | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 7:00 | 3.9 | Thu | School Day | On | On | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 5.0001
| 8:00 | 4.2 | Thu | School Day | On | On | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 4.9172
| 9:00 | 4.4 | Thu | School Day | On | On | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 4.8619
| 10:00 | 5.1 | Thu | School Day | On | On | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 4.6686
| 11:00 | 5.9 | Thu | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 12:00 | 5.9 | Thu | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 13:00 | 7.1 | Thu | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 14:00 | 7.7 | Thu | School Day | On | On | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 3.9503
| 15:00 | 7.9 | Thu | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 16:00 | 8.6 | Thu | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 17:00 | 9.2 | Thu | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 18:00 | 8.8 | Thu | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 19:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 20:00 | 6.8 | Thu | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 21:00 | 5 | Thu | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 22:00 | 4.3 | Thu | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 23:00 | 3.3 | Thu | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
Fri, 18/Mar | 24:00 | 2.5 | Fri | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 1:00 | 1.4 | Fri | School Day | Off | Off | 22 | 19.94 | 2.06 | 1.7 | 3.9348 | 0.25 | 1035 | 1.7559 | 0
| 2:00 | 0.6 | Fri | School Day | Off | Off | 22 | 19.86 | 2.14 | 1.7 | 4.0876 | 0.25 | 1035 | 1.8241 | 0
| 3:00 | 0.2 | Fri | School Day | Off | Off | 22 | 19.82 | 2.18 | 1.7 | 4.164 | 0.25 | 1035 | 1.8582 | 0
| 4:00 | -0.4 | Fri | School Day | Off | Off | 22 | 19.76 | 2.24 | 1.7 | 4.2786 | 0.25 | 1035 | 1.9093 | 0
| 5:00 | -1.2 | Fri | School Day | Off | Off | 22 | 19.68 | 2.32 | 1.7 | 4.4314 | 0.25 | 1035 | 1.9775 | 0
| 6:00 | -1.5 | Fri | School Day | Off | Off | 22 | 19.65 | 2.35 | 1.7 | 4.4887 | 0.25 | 1035 | 2.0031 | 0
| 7:00 | -1.9 | Fri | School Day | On | On | 22 | 19.61 | 2.39 | 1.7 | 4.5651 | 0.25 | 1035 | 2.0372 | 6.6023
| 8:00 | -1.5 | Fri | School Day | On | On | 22 | 19.65 | 2.35 | 1.7 | 4.4887 | 0.25 | 1035 | 2.0031 | 6.4918
| 9:00 | 2 | Fri | School Day | On | On | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 5.5249
| 10:00 | 4.8 | Fri | School Day | On | On | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 4.7514
| 11:00 | 6.9 | Fri | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 12:00 | 8.4 | Fri | School Day | On | On | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 3.757
| 13:00 | 10 | Fri | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 14:00 | 10.6 | Fri | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 15:00 | 10 | Fri | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 16:00 | 9.4 | Fri | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 17:00 | 9.5 | Fri | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 18:00 | 9.1 | Fri | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 19:00 | 8.1 | Fri | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 20:00 | 7.7 | Fri | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 21:00 | 8.1 | Fri | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 22:00 | 7.8 | Fri | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 23:00 | 8 | Fri | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
Sat, 19/Mar | 24:00 | 8.5 | Sat | WE | Off | OFF | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 1:00 | 8.5 | Sat | WE | Off | OFF | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 2:00 | 8.7 | Sat | WE | Off | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 3:00 | 9.1 | Sat | WE | Off | OFF | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 4:00 | 9.5 | Sat | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 5:00 | 9.9 | Sat | WE | Off | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 6:00 | 10.1 | Sat | WE | Off | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 7:00 | 10.1 | Sat | WE | On | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 8:00 | 10.4 | Sat | WE | On | OFF | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 9:00 | 10.9 | Sat | WE | On | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 10:00 | 11.6 | Sat | WE | On | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 11:00 | 12 | Sat | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 12:00 | 12.3 | Sat | WE | On | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 13:00 | 12.2 | Sat | WE | On | OFF | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 14:00 | 14 | Sat | WE | On | OFF | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 15:00 | 13.8 | Sat | WE | On | OFF | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 16:00 | 12.9 | Sat | WE | On | OFF | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 17:00 | 12.3 | Sat | WE | On | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 18:00 | 12.4 | Sat | WE | On | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 19:00 | 11.8 | Sat | WE | Off | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 20:00 | 11.6 | Sat | WE | Off | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 21:00 | 11.5 | Sat | WE | Off | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 22:00 | 11.2 | Sat | WE | Off | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 23:00 | 11.3 | Sat | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
Sun, 20/Mar | 24:00 | 11.3 | Sun | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 1:00 | 11 | Sun | WE | Off | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 2:00 | 7.8 | Sun | WE | Off | OFF | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 3:00 | 7.2 | Sun | WE | Off | OFF | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 4:00 | 6.3 | Sun | WE | Off | OFF | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 5:00 | 6.6 | Sun | WE | Off | OFF | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 6:00 | 6.2 | Sun | WE | Off | OFF | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 7:00 | 4.8 | Sun | WE | On | OFF | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 8:00 | 4.9 | Sun | WE | On | OFF | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 9:00 | 6.2 | Sun | WE | On | OFF | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 10:00 | 7.5 | Sun | WE | On | OFF | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 11:00 | 8.1 | Sun | WE | On | OFF | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 12:00 | 9.4 | Sun | WE | On | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 13:00 | 10.9 | Sun | WE | On | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 14:00 | 10.8 | Sun | WE | On | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 15:00 | 11.6 | Sun | WE | On | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 16:00 | 12 | Sun | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 17:00 | 11.1 | Sun | WE | On | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 18:00 | 9.5 | Sun | WE | On | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 19:00 | 7.1 | Sun | WE | Off | OFF | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 20:00 | 6.6 | Sun | WE | Off | OFF | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 21:00 | 6 | Sun | WE | Off | OFF | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 22:00 | 5.6 | Sun | WE | Off | OFF | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 23:00 | 3.8 | Sun | WE | Off | OFF | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
Mon, 21/Mar | 24:00 | 3.8 | Mon | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 1:00 | 4.1 | Mon | School Day | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 2:00 | 3.8 | Mon | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 3:00 | 3.1 | Mon | School Day | Off | Off | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 4:00 | 2.8 | Mon | School Day | Off | Off | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 5:00 | 2 | Mon | School Day | Off | Off | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 0
| 6:00 | 2.4 | Mon | School Day | Off | Off | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 7:00 | 2 | Mon | School Day | On | On | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 5.5249
| 8:00 | 2.8 | Mon | School Day | On | On | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 5.3039
| 9:00 | 3.5 | Mon | School Day | On | On | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 5.1106
| 10:00 | 5.4 | Mon | School Day | On | On | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 4.5857
| 11:00 | 6.7 | Mon | School Day | On | On | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 4.2266
| 12:00 | 8.4 | Mon | School Day | On | On | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 3.757
| 13:00 | 8.7 | Mon | School Day | On | On | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 3.6741
| 14:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 15:00 | 7.5 | Mon | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 16:00 | 8.1 | Mon | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 17:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 18:00 | 9 | Mon | School Day | On | On | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 3.5912
| 19:00 | 10.1 | Mon | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 20:00 | 10.9 | Mon | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 21:00 | 11.6 | Mon | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 22:00 | 11.6 | Mon | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 23:00 | 11.6 | Mon | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
Tue, 22/Mar | 24:00 | 11.8 | Tue | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 1:00 | 11.9 | Tue | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 2:00 | 12.3 | Tue | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 3:00 | 11.8 | Tue | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 4:00 | 11.6 | Tue | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 5:00 | 11.3 | Tue | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 6:00 | 11.5 | Tue | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 7:00 | 11.5 | Tue | School Day | On | On | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 2.9006
| 8:00 | 11.5 | Tue | School Day | On | On | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 2.9006
| 9:00 | 12 | Tue | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 10:00 | 12.2 | Tue | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 11:00 | 12.3 | Tue | School Day | On | On | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 2.6796
| 12:00 | 13 | Tue | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 13:00 | 14.1 | Tue | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 14:00 | 13.8 | Tue | School Day | On | On | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 2.2652
| 15:00 | 14.1 | Tue | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 16:00 | 12.6 | Tue | School Day | On | On | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 2.5967
| 17:00 | 10.9 | Tue | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 18:00 | 9.7 | Tue | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 19:00 | 9.3 | Tue | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 20:00 | 7.1 | Tue | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 21:00 | 5.9 | Tue | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 22:00 | 5 | Tue | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 23:00 | 3.9 | Tue | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
Wed, 23/Mar | 24:00 | 3.9 | Wed | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 1:00 | 3.6 | Wed | School Day | Off | Off | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 2:00 | 3.5 | Wed | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 3:00 | 2.9 | Wed | School Day | Off | Off | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 4:00 | 2.3 | Wed | School Day | Off | Off | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 0
| 5:00 | 2.3 | Wed | School Day | Off | Off | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 0
| 6:00 | 2 | Wed | School Day | Off | Off | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 0
| 7:00 | 2.2 | Wed | School Day | On | On | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 5.4697
| 8:00 | 2.3 | Wed | School Day | On | On | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 5.4421
| 9:00 | 4.7 | Wed | School Day | On | On | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 4.7791
| 10:00 | 6.8 | Wed | School Day | On | On | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 4.199
| 11:00 | 8.1 | Wed | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 12:00 | 8.4 | Wed | School Day | On | On | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 3.757
| 13:00 | 8.5 | Wed | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 14:00 | 8.8 | Wed | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 15:00 | 8.8 | Wed | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 16:00 | 9 | Wed | School Day | On | On | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 3.5912
| 17:00 | 8.9 | Wed | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 18:00 | 8.2 | Wed | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 19:00 | 8.5 | Wed | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 20:00 | 8.7 | Wed | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 21:00 | 8.8 | Wed | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 22:00 | 8.5 | Wed | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 23:00 | 8.7 | Wed | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
Thu, 24/Mar | 24:00 | 8.9 | Thu | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 1:00 | 9 | Thu | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 2:00 | 9.5 | Thu | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 3:00 | 9.8 | Thu | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 4:00 | 9.6 | Thu | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 5:00 | 9.9 | Thu | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 6:00 | 10.3 | Thu | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 7:00 | 10.6 | Thu | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 8:00 | 10.7 | Thu | School Day | On | On | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 3.1216
| 9:00 | 11.4 | Thu | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 10:00 | 11.9 | Thu | School Day | On | On | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 2.7901
| 11:00 | 12.5 | Thu | School Day | On | On | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 2.6243
| 12:00 | 12.8 | Thu | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 13:00 | 14.4 | Thu | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 14:00 | 15 | Thu | School Day | On | On | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 1.9337
| 15:00 | 15.5 | Thu | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 16:00 | 14.2 | Thu | School Day | On | On | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 2.1547
| 17:00 | 13.2 | Thu | School Day | On | On | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 2.431
| 18:00 | 12.3 | Thu | School Day | On | On | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 2.6796
| 19:00 | 11.4 | Thu | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 20:00 | 10.3 | Thu | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 21:00 | 9.4 | Thu | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 22:00 | 8.9 | Thu | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 23:00 | 8.7 | Thu | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
Fri, 25/Mar | 24:00 | 8.7 | Fri | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 1:00 | 7.7 | Fri | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 2:00 | 6.8 | Fri | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 3:00 | 5.8 | Fri | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 4:00 | 4.4 | Fri | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 5:00 | 3.2 | Fri | School Day | Off | Off | 22 | 20.12 | 1.88 | 1.7 | 3.591 | 0.25 | 1035 | 1.6024 | 0
| 6:00 | 3.3 | Fri | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 7:00 | 3.1 | Fri | School Day | On | On | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 5.2211
| 8:00 | 3.4 | Fri | School Day | On | On | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 5.1382
| 9:00 | 6.4 | Fri | School Day | On | On | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 4.3095
| 10:00 | 8.1 | Fri | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 11:00 | 9.7 | Fri | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 12:00 | 10.7 | Fri | School Day | On | On | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 3.1216
| 13:00 | 11.1 | Fri | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 14:00 | 11.6 | Fri | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 15:00 | 12.3 | Fri | School Day | On | On | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 2.6796
| 16:00 | 12.2 | Fri | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 17:00 | 12.1 | Fri | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 18:00 | 12.1 | Fri | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 19:00 | 10.9 | Fri | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 20:00 | 9.8 | Fri | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 21:00 | 9.8 | Fri | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 22:00 | 9.5 | Fri | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 23:00 | 9.8 | Fri | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
Sat, 26/Mar | 24:00 | 9.9 | Sat | WE | Off | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 1:00 | 9.6 | Sat | WE | Off | OFF | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 2:00 | 9 | Sat | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 3:00 | 9.1 | Sat | WE | Off | OFF | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 4:00 | 8.3 | Sat | WE | Off | OFF | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 5:00 | 8.2 | Sat | WE | Off | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 6:00 | 7.9 | Sat | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 7:00 | 8.5 | Sat | WE | On | OFF | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 8:00 | 9 | Sat | WE | On | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 9:00 | 10.1 | Sat | WE | On | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 10:00 | 11.9 | Sat | WE | On | OFF | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 11:00 | 12.6 | Sat | WE | On | OFF | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 12:00 | 14.2 | Sat | WE | On | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 13:00 | 16.3 | Sat | WE | On | OFF | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 14:00 | 17.3 | Sat | WE | On | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 15:00 | 17 | Sat | WE | On | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 16:00 | 17.8 | Sat | WE | On | OFF | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 17:00 | 17.1 | Sat | WE | On | OFF | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 18:00 | 16.4 | Sat | WE | On | OFF | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 19:00 | 15.4 | Sat | WE | Off | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 20:00 | 13 | Sat | WE | Off | OFF | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 21:00 | 11.8 | Sat | WE | Off | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 22:00 | 11.5 | Sat | WE | Off | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 23:00 | 11.3 | Sat | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
Sun, 27/Mar | 24:00 | 10.5 | Sun | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 1:00 | 11.4 | Sun | WE | Off | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 2:00 | 11.2 | Sun | WE | Off | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 3:00 | 10.3 | Sun | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 4:00 | 10.6 | Sun | WE | Off | OFF | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 5:00 | 9.9 | Sun | WE | Off | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 6:00 | 8.4 | Sun | WE | Off | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 7:00 | 9.3 | Sun | WE | On | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 8:00 | 9.2 | Sun | WE | On | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 9:00 | 12.1 | Sun | WE | On | OFF | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 10:00 | 13.9 | Sun | WE | On | OFF | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 11:00 | 15.9 | Sun | WE | On | OFF | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 12:00 | 15.8 | Sun | WE | On | OFF | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 13:00 | 15.4 | Sun | WE | On | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 14:00 | 16.5 | Sun | WE | On | OFF | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 15:00 | 17.7 | Sun | WE | On | OFF | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 16:00 | 19.7 | Sun | WE | On | OFF | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 17:00 | 19.6 | Sun | WE | On | OFF | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 18:00 | 18.4 | Sun | WE | On | OFF | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 19:00 | 17.3 | Sun | WE | Off | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 20:00 | 16.3 | Sun | WE | Off | OFF | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 21:00 | 15.1 | Sun | WE | Off | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 22:00 | 13.6 | Sun | WE | Off | OFF | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 23:00 | 13 | Sun | WE | Off | OFF | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
Mon, 28/Mar | 24:00 | 11.3 | Mon | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 1:00 | 10.3 | Mon | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 2:00 | 10.3 | Mon | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 3:00 | 10 | Mon | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 4:00 | 10.8 | Mon | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 5:00 | 10.6 | Mon | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 6:00 | 9.8 | Mon | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 7:00 | 10.3 | Mon | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 8:00 | 11.7 | Mon | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 9:00 | 13.9 | Mon | School Day | On | On | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 2.2376
| 10:00 | 14.5 | Mon | School Day | On | On | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 2.0719
| 11:00 | 16.6 | Mon | School Day | On | On | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 1.4917
| 12:00 | 18.1 | Mon | School Day | On | On | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 1.0774
| 13:00 | 19.6 | Mon | School Day | On | On | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0.66299
| 14:00 | 14.6 | Mon | School Day | On | On | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 2.0442
| 15:00 | 13.3 | Mon | School Day | On | On | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 2.4033
| 16:00 | 13.3 | Mon | School Day | On | On | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 2.4033
| 17:00 | 12.7 | Mon | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 18:00 | 12.1 | Mon | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 19:00 | 11.3 | Mon | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 20:00 | 10.7 | Mon | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 21:00 | 10.1 | Mon | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 22:00 | 9.9 | Mon | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 23:00 | 9.5 | Mon | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
Tue, 29/Mar | 24:00 | 9.3 | Tue | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 1:00 | 9.3 | Tue | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 2:00 | 9.2 | Tue | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 3:00 | 9.1 | Tue | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 4:00 | 9.2 | Tue | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 5:00 | 8.8 | Tue | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 6:00 | 9 | Tue | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 7:00 | 8.8 | Tue | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 8:00 | 9.1 | Tue | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 9:00 | 9.3 | Tue | School Day | On | On | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 3.5083
| 10:00 | 10 | Tue | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 11:00 | 10.9 | Tue | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 12:00 | 11.9 | Tue | School Day | On | On | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 2.7901
| 13:00 | 13.2 | Tue | School Day | On | On | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 2.431
| 14:00 | 14.4 | Tue | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 15:00 | 15.3 | Tue | School Day | On | On | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 1.8509
| 16:00 | 15.6 | Tue | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 17:00 | 15.8 | Tue | School Day | On | On | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 1.7127
| 18:00 | 14.5 | Tue | School Day | On | On | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 2.0719
| 19:00 | 13.2 | Tue | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 20:00 | 12.7 | Tue | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 21:00 | 11.9 | Tue | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 22:00 | 11.7 | Tue | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 23:00 | 11.8 | Tue | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
Wed, 30/Mar | 24:00 | 9.8 | Wed | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 1:00 | 9.7 | Wed | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 2:00 | 8.1 | Wed | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 3:00 | 8.2 | Wed | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 4:00 | 8.8 | Wed | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 5:00 | 7.2 | Wed | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 6:00 | 7.8 | Wed | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 7:00 | 7 | Wed | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 8:00 | 7.2 | Wed | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 9:00 | 8.2 | Wed | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 10:00 | 10 | Wed | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 11:00 | 12.6 | Wed | School Day | On | On | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 2.5967
| 12:00 | 14.9 | Wed | School Day | On | On | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 1.9614
| 13:00 | 16.8 | Wed | School Day | On | On | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 1.4365
| 14:00 | 18.5 | Wed | School Day | On | On | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0.96686
| 15:00 | 18.8 | Wed | School Day | On | On | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0.88399
| 16:00 | 19.2 | Wed | School Day | On | On | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0.77349
| 17:00 | 19.1 | Wed | School Day | On | On | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0.80112
| 18:00 | 18.5 | Wed | School Day | On | On | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0.96686
| 19:00 | 16.9 | Wed | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 20:00 | 16.2 | Wed | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 21:00 | 14.9 | Wed | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 22:00 | 13.3 | Wed | School Day | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 23:00 | 12.5 | Wed | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
Thu, 31/Mar | 24:00 | 10.3 | Thu | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 1:00 | 10.1 | Thu | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 2:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 3:00 | 8.1 | Thu | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 4:00 | 8.3 | Thu | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 5:00 | 7.4 | Thu | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 6:00 | 6.9 | Thu | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 7:00 | 6.3 | Thu | School Day | On | On | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 4.3371
| 8:00 | 6.1 | Thu | School Day | On | On | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 4.3923
| 9:00 | 8.1 | Thu | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 10:00 | 10.3 | Thu | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 11:00 | 14 | Thu | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 12:00 | 15.8 | Thu | School Day | On | On | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 1.7127
| 13:00 | 17.5 | Thu | School Day | On | On | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 1.2431
| 14:00 | 18.3 | Thu | School Day | On | On | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 1.0221
| 15:00 | 18.9 | Thu | School Day | On | On | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0.85637
| 16:00 | 19.5 | Thu | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 17:00 | 19.8 | Thu | School Day | On | On | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0.60774
| 18:00 | 19.5 | Thu | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 19:00 | 18.5 | Thu | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 20:00 | 15.2 | Thu | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 21:00 | 13.9 | Thu | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 22:00 | 13.4 | Thu | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 23:00 | 11.1 | Thu | School Day | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
Fri, 01/Apr | 24:00 | 10.6 | Fri | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 1:00 | 10.5 | Fri | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 2:00 | 10.5 | Fri | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 3:00 | 10.8 | Fri | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 4:00 | 10.9 | Fri | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 5:00 | 10.5 | Fri | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 6:00 | 9.8 | Fri | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 7:00 | 9.4 | Fri | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 8:00 | 9.5 | Fri | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 9:00 | 9.5 | Fri | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 10:00 | 10.2 | Fri | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 11:00 | 11.8 | Fri | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 12:00 | 13.2 | Fri | School Day | On | On | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 2.431
| 13:00 | 14.4 | Fri | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 14:00 | 14.1 | Fri | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 15:00 | 13.9 | Fri | School Day | On | On | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 2.2376
| 16:00 | 14.8 | Fri | School Day | On | On | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 1.989
| 17:00 | 14.9 | Fri | School Day | On | On | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 1.9614
| 18:00 | 14.3 | Fri | School Day | On | On | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 2.1271
| 19:00 | 12.9 | Fri | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 20:00 | 11.3 | Fri | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 21:00 | 8.9 | Fri | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 22:00 | 8.7 | Fri | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 23:00 | 9 | Fri | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
Sat, 02/Apr | 24:00 | 9.2 | Sat | WE | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 1:00 | 9.4 | Sat | WE | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 2:00 | 9.6 | Sat | WE | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 3:00 | 9.5 | Sat | WE | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 4:00 | 9.5 | Sat | WE | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 5:00 | 9.4 | Sat | WE | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 6:00 | 9.2 | Sat | WE | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 7:00 | 8.7 | Sat | WE | On | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 8:00 | 8.5 | Sat | WE | On | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 9:00 | 8.5 | Sat | WE | On | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 10:00 | 8.5 | Sat | WE | On | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 11:00 | 8.4 | Sat | WE | On | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 12:00 | 8.5 | Sat | WE | On | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 13:00 | 8.4 | Sat | WE | On | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 14:00 | 9.2 | Sat | WE | On | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 15:00 | 9.9 | Sat | WE | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 16:00 | 10.3 | Sat | WE | On | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 17:00 | 11.5 | Sat | WE | On | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 18:00 | 11.4 | Sat | WE | On | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 19:00 | 10.6 | Sat | WE | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 20:00 | 9.3 | Sat | WE | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 21:00 | 7.7 | Sat | WE | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 22:00 | 7.2 | Sat | WE | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 23:00 | 7.1 | Sat | WE | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
Sun, 03/Apr | 24:00 | 6.2 | Sun | WE | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 1:00 | 5.6 | Sun | WE | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 2:00 | 5.6 | Sun | WE | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 3:00 | 5.6 | Sun | WE | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 4:00 | 5.6 | Sun | WE | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 5:00 | 5.2 | Sun | WE | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 6:00 | 4.9 | Sun | WE | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 7:00 | 5.2 | Sun | WE | On | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 8:00 | 5.1 | Sun | WE | On | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 9:00 | 5.3 | Sun | WE | On | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 10:00 | 5.6 | Sun | WE | On | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 11:00 | 7 | Sun | WE | On | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 12:00 | 7.1 | Sun | WE | On | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 13:00 | 7.9 | Sun | WE | On | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 14:00 | 7.3 | Sun | WE | On | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 15:00 | 7.9 | Sun | WE | On | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 16:00 | 7.4 | Sun | WE | On | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 17:00 | 8.2 | Sun | WE | On | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 18:00 | 7.3 | Sun | WE | On | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 19:00 | 6.9 | Sun | WE | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 20:00 | 5.9 | Sun | WE | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 21:00 | 5.3 | Sun | WE | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 22:00 | 4.8 | Sun | WE | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 23:00 | 4.1 | Sun | WE | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
Mon, 04/Apr | 24:00 | 3.8 | Mon | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 1:00 | 3.7 | Mon | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 2:00 | 3.9 | Mon | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 3:00 | 4.2 | Mon | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 4:00 | 3.8 | Mon | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 5:00 | 3.7 | Mon | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 6:00 | 3.4 | Mon | School Day | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 7:00 | 3.1 | Mon | School Day | On | Off | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 8:00 | 2.6 | Mon | School Day | On | Off | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 0
| 9:00 | 3 | Mon | School Day | On | Off | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 10:00 | 3.8 | Mon | School Day | On | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 11:00 | 4.5 | Mon | School Day | On | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 12:00 | 6.3 | Mon | School Day | On | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 13:00 | 6.4 | Mon | School Day | On | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 14:00 | 7.6 | Mon | School Day | On | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 15:00 | 7 | Mon | School Day | On | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 16:00 | 6.6 | Mon | School Day | On | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 17:00 | 6.2 | Mon | School Day | On | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 18:00 | 3.8 | Mon | School Day | On | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 19:00 | 2.4 | Mon | School Day | Off | Off | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 20:00 | 2.2 | Mon | School Day | Off | Off | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 0
| 21:00 | 2.9 | Mon | School Day | Off | Off | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 22:00 | 3.3 | Mon | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 23:00 | 3.7 | Mon | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
Tue, 05/Apr | 24:00 | 4.2 | Tue | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 1:00 | 4.7 | Tue | School Day | Off | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 2:00 | 5.1 | Tue | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 3:00 | 5.3 | Tue | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 4:00 | 5.6 | Tue | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 5:00 | 5.8 | Tue | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 6:00 | 5.9 | Tue | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 7:00 | 5.9 | Tue | School Day | On | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 8:00 | 5.3 | Tue | School Day | On | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 9:00 | 3.5 | Tue | School Day | On | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 10:00 | 1.7 | Tue | School Day | On | Off | 22 | 19.97 | 2.03 | 1.7 | 3.8775 | 0.25 | 1035 | 1.7303 | 0
| 11:00 | 1.7 | Tue | School Day | On | Off | 22 | 19.97 | 2.03 | 1.7 | 3.8775 | 0.25 | 1035 | 1.7303 | 0
| 12:00 | 1.7 | Tue | School Day | On | Off | 22 | 19.97 | 2.03 | 1.7 | 3.8775 | 0.25 | 1035 | 1.7303 | 0
| 13:00 | 2.6 | Tue | School Day | On | Off | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 0
| 14:00 | 3.1 | Tue | School Day | On | Off | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 15:00 | 3.7 | Tue | School Day | On | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 16:00 | 4.8 | Tue | School Day | On | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 17:00 | 5 | Tue | School Day | On | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 18:00 | 5.1 | Tue | School Day | On | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 19:00 | 4.3 | Tue | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 20:00 | 4.1 | Tue | School Day | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 21:00 | 4.1 | Tue | School Day | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 22:00 | 4.2 | Tue | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 23:00 | 3.7 | Tue | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
Wed, 06/Apr | 24:00 | 3.6 | Wed | School Day | Off | Off | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 1:00 | 3.5 | Wed | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 2:00 | 3.3 | Wed | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 3:00 | 3.4 | Wed | School Day | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 4:00 | 3.3 | Wed | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 5:00 | 3.8 | Wed | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 6:00 | 3.8 | Wed | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 7:00 | 3.6 | Wed | School Day | On | Off | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 8:00 | 3.8 | Wed | School Day | On | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 9:00 | 3.9 | Wed | School Day | On | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 10:00 | 4.4 | Wed | School Day | On | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 11:00 | 4.7 | Wed | School Day | On | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 12:00 | 4.9 | Wed | School Day | On | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 13:00 | 5.3 | Wed | School Day | On | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 14:00 | 5.8 | Wed | School Day | On | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 15:00 | 6.1 | Wed | School Day | On | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 16:00 | 6.4 | Wed | School Day | On | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 17:00 | 6.3 | Wed | School Day | On | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 18:00 | 6.2 | Wed | School Day | On | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 19:00 | 6.7 | Wed | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 20:00 | 6.4 | Wed | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 21:00 | 6.2 | Wed | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 22:00 | 5.8 | Wed | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 23:00 | 5.7 | Wed | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
Thu, 07/Apr | 24:00 | 5.6 | Thu | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 1:00 | 5.9 | Thu | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 2:00 | 5.5 | Thu | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 3:00 | 4.7 | Thu | School Day | Off | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 4:00 | 4.9 | Thu | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 5:00 | 4.7 | Thu | School Day | Off | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 6:00 | 4.3 | Thu | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 7:00 | 4.2 | Thu | School Day | On | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 8:00 | 4.3 | Thu | School Day | On | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 9:00 | 4.9 | Thu | School Day | On | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 10:00 | 7 | Thu | School Day | On | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 11:00 | 8.4 | Thu | School Day | On | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 12:00 | 10.5 | Thu | School Day | On | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 13:00 | 11 | Thu | School Day | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 14:00 | 10.8 | Thu | School Day | On | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 15:00 | 12.4 | Thu | School Day | On | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 16:00 | 9.9 | Thu | School Day | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 17:00 | 10.8 | Thu | School Day | On | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 18:00 | 10.6 | Thu | School Day | On | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 19:00 | 10 | Thu | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 20:00 | 10.1 | Thu | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 21:00 | 9.3 | Thu | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 22:00 | 8.5 | Thu | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 23:00 | 7.7 | Thu | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
Fri, 08/Apr | 24:00 | 7 | Fri | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 1:00 | 5.9 | Fri | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 2:00 | 4.6 | Fri | School Day | Off | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 3:00 | 3.7 | Fri | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 4:00 | 3.9 | Fri | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 5:00 | 3.4 | Fri | School Day | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 6:00 | 3.2 | Fri | School Day | Off | Off | 22 | 20.12 | 1.88 | 1.7 | 3.591 | 0.25 | 1035 | 1.6024 | 0
| 7:00 | 1.8 | Fri | School Day | On | Off | 22 | 19.98 | 2.02 | 1.7 | 3.8584 | 0.25 | 1035 | 1.7218 | 0
| 8:00 | 2.4 | Fri | School Day | On | Off | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 9:00 | 3.7 | Fri | School Day | On | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 10:00 | 6.2 | Fri | School Day | On | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 11:00 | 8.9 | Fri | School Day | On | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 12:00 | 10.6 | Fri | School Day | On | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 13:00 | 11.3 | Fri | School Day | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 14:00 | 12.2 | Fri | School Day | On | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 15:00 | 12.8 | Fri | School Day | On | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 16:00 | 12.8 | Fri | School Day | On | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 17:00 | 12.9 | Fri | School Day | On | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 18:00 | 13.2 | Fri | School Day | On | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 19:00 | 12.9 | Fri | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 20:00 | 11.5 | Fri | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 21:00 | 8.9 | Fri | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 22:00 | 8.4 | Fri | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 23:00 | 7.6 | Fri | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
Sat, 09/Apr | 24:00 | 7.4 | Sat | WE | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 1:00 | 5.6 | Sat | WE | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 2:00 | 5.2 | Sat | WE | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 3:00 | 4.7 | Sat | WE | Off | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 4:00 | 4.4 | Sat | WE | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 5:00 | 3.9 | Sat | WE | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 6:00 | 2.9 | Sat | WE | Off | Off | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 7:00 | 2.4 | Sat | WE | On | Off | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 8:00 | 2 | Sat | WE | On | Off | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 0
| 9:00 | 3.8 | Sat | WE | On | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 10:00 | 7.2 | Sat | WE | On | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 11:00 | 9.7 | Sat | WE | On | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 12:00 | 10.6 | Sat | WE | On | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 13:00 | 11.9 | Sat | WE | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 14:00 | 13.4 | Sat | WE | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 15:00 | 14.3 | Sat | WE | On | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 16:00 | 14.8 | Sat | WE | On | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 17:00 | 14.8 | Sat | WE | On | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 18:00 | 14.3 | Sat | WE | On | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 19:00 | 13.6 | Sat | WE | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 20:00 | 13.2 | Sat | WE | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 21:00 | 13 | Sat | WE | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 22:00 | 12.1 | Sat | WE | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 23:00 | 11.1 | Sat | WE | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
Sun, 10/Apr | 24:00 | 11 | Sun | WE | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 1:00 | 11 | Sun | WE | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 2:00 | 10.6 | Sun | WE | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 3:00 | 10.8 | Sun | WE | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 4:00 | 10.5 | Sun | WE | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 5:00 | 10.9 | Sun | WE | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 6:00 | 11.4 | Sun | WE | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 7:00 | 11.6 | Sun | WE | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 8:00 | 11.7 | Sun | WE | On | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 9:00 | 11.5 | Sun | WE | On | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 10:00 | 11.2 | Sun | WE | On | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 11:00 | 11 | Sun | WE | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 12:00 | 11.3 | Sun | WE | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 13:00 | 13.6 | Sun | WE | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 14:00 | 14.2 | Sun | WE | On | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 15:00 | 13.9 | Sun | WE | On | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 16:00 | 12.6 | Sun | WE | On | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 17:00 | 12.3 | Sun | WE | On | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 18:00 | 13.4 | Sun | WE | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 19:00 | 8.7 | Sun | WE | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 20:00 | 9.9 | Sun | WE | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 21:00 | 9.7 | Sun | WE | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 22:00 | 9.8 | Sun | WE | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 23:00 | 8.8 | Sun | WE | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
Mon, 11/Apr | 24:00 | 8.5 | Mon | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 1:00 | 8.1 | Mon | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 2:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 3:00 | 8.5 | Mon | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 4:00 | 8.3 | Mon | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 5:00 | 8.4 | Mon | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 6:00 | 9.2 | Mon | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 7:00 | 9.2 | Mon | School Day | On | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 8:00 | 9.7 | Mon | School Day | On | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 9:00 | 10.6 | Mon | School Day | On | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 10:00 | 11 | Mon | School Day | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 11:00 | 11.2 | Mon | School Day | On | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 12:00 | 11.3 | Mon | School Day | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 13:00 | 10.9 | Mon | School Day | On | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 14:00 | 11.5 | Mon | School Day | On | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 15:00 | 11.6 | Mon | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 16:00 | 12.8 | Mon | School Day | On | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 17:00 | 13.8 | Mon | School Day | On | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 18:00 | 13.4 | Mon | School Day | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 19:00 | 13.2 | Mon | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 20:00 | 12.3 | Mon | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 21:00 | 11.4 | Mon | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 22:00 | 10.5 | Mon | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 23:00 | 10.2 | Mon | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
Tue, 12/Apr | 24:00 | 9.7 | Tue | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 1:00 | 9.7 | Tue | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 2:00 | 9.2 | Tue | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 3:00 | 8.5 | Tue | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 4:00 | 7.6 | Tue | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 5:00 | 7.4 | Tue | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 6:00 | 6.7 | Tue | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 7:00 | 6.7 | Tue | School Day | On | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 8:00 | 5.5 | Tue | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 9:00 | 7.9 | Tue | School Day | On | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 10:00 | 10 | Tue | School Day | On | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 11:00 | 11.1 | Tue | School Day | On | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 12:00 | 11.6 | Tue | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 13:00 | 11.6 | Tue | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 14:00 | 12.9 | Tue | School Day | On | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 15:00 | 12.6 | Tue | School Day | On | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 16:00 | 13.3 | Tue | School Day | On | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 17:00 | 13.2 | Tue | School Day | On | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 18:00 | 12.6 | Tue | School Day | On | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 19:00 | 12.8 | Tue | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 20:00 | 12.3 | Tue | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 21:00 | 11.2 | Tue | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 22:00 | 10.8 | Tue | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 23:00 | 10.3 | Tue | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
Wed, 13/Apr | 24:00 | 9.9 | Wed | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 1:00 | 9.3 | Wed | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 2:00 | 9.1 | Wed | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 3:00 | 8.1 | Wed | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 4:00 | 8.4 | Wed | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 5:00 | 8.2 | Wed | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 6:00 | 8.1 | Wed | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 7:00 | 8 | Wed | School Day | On | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 8:00 | 8 | Wed | School Day | On | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 9:00 | 8.8 | Wed | School Day | On | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 10:00 | 9.9 | Wed | School Day | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 11:00 | 10.3 | Wed | School Day | On | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 12:00 | 11.3 | Wed | School Day | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 13:00 | 11.9 | Wed | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 14:00 | 12.3 | Wed | School Day | On | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 15:00 | 13.6 | Wed | School Day | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 16:00 | 14.6 | Wed | School Day | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 17:00 | 14.5 | Wed | School Day | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 18:00 | 14.1 | Wed | School Day | On | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 19:00 | 14.1 | Wed | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 20:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 21:00 | 12.7 | Wed | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 22:00 | 11.2 | Wed | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 23:00 | 8.6 | Wed | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
Thu, 14/Apr | 24:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 1:00 | 7.8 | Thu | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 2:00 | 8 | Thu | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 3:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 4:00 | 7.2 | Thu | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 5:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 6:00 | 6.7 | Thu | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 7:00 | 6.7 | Thu | School Day | On | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 8:00 | 6.6 | Thu | School Day | On | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 9:00 | 6.7 | Thu | School Day | On | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 10:00 | 7.5 | Thu | School Day | On | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 11:00 | 9.1 | Thu | School Day | On | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 12:00 | 11.3 | Thu | School Day | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 13:00 | 11.9 | Thu | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 14:00 | 12 | Thu | School Day | On | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 15:00 | 14 | Thu | School Day | On | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 16:00 | 14 | Thu | School Day | On | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 17:00 | 13.6 | Thu | School Day | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 18:00 | 13.6 | Thu | School Day | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 19:00 | 13.9 | Thu | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 20:00 | 12.8 | Thu | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 21:00 | 12 | Thu | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 22:00 | 9.8 | Thu | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 23:00 | 9.2 | Thu | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
Fri, 15/Apr | 24:00 | 8.1 | Fri | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 1:00 | 6.4 | Fri | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 2:00 | 6.8 | Fri | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 3:00 | 6.2 | Fri | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 4:00 | 5 | Fri | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 5:00 | 4.8 | Fri | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 6:00 | 3.9 | Fri | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 7:00 | 3.8 | Fri | School Day | On | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 8:00 | 3.9 | Fri | School Day | On | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 9:00 | 5.4 | Fri | School Day | On | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 10:00 | 6.8 | Fri | School Day | On | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 11:00 | 9.4 | Fri | School Day | On | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 12:00 | 11.4 | Fri | School Day | On | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 13:00 | 12 | Fri | School Day | On | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 14:00 | 13.5 | Fri | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 15:00 | 13.1 | Fri | School Day | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 16:00 | 14.9 | Fri | School Day | On | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 17:00 | 14.6 | Fri | School Day | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 18:00 | 13.3 | Fri | School Day | On | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 19:00 | 13.8 | Fri | School Day | Off | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 20:00 | 12.6 | Fri | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 21:00 | 12 | Fri | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 22:00 | 11.8 | Fri | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 23:00 | 10.6 | Fri | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
Sat, 16/Apr | 24:00 | 10.7 | Sat | WE | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 1:00 | 11 | Sat | WE | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 2:00 | 11 | Sat | WE | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 3:00 | 10.7 | Sat | WE | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 4:00 | 10.3 | Sat | WE | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 5:00 | 10.2 | Sat | WE | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 6:00 | 10.1 | Sat | WE | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 7:00 | 10 | Sat | WE | On | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 8:00 | 10.2 | Sat | WE | On | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 9:00 | 10.6 | Sat | WE | On | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 10:00 | 11 | Sat | WE | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 11:00 | 11.7 | Sat | WE | On | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 12:00 | 12.2 | Sat | WE | On | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 13:00 | 12.3 | Sat | WE | On | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 14:00 | 12.5 | Sat | WE | On | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 15:00 | 11.9 | Sat | WE | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 16:00 | 10.7 | Sat | WE | On | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 17:00 | 10.8 | Sat | WE | On | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 18:00 | 9.9 | Sat | WE | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 19:00 | 8.7 | Sat | WE | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 20:00 | 8.3 | Sat | WE | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 21:00 | 8.2 | Sat | WE | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 22:00 | 8 | Sat | WE | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 23:00 | 8 | Sat | WE | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
Sun, 17/Apr | 24:00 | 8.1 | Sun | WE | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 1:00 | 8 | Sun | WE | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 2:00 | 8.4 | Sun | WE | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 3:00 | 8.6 | Sun | WE | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 4:00 | 8.6 | Sun | WE | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 5:00 | 8.7 | Sun | WE | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 6:00 | 8.5 | Sun | WE | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 7:00 | 8.6 | Sun | WE | On | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 8:00 | 8.8 | Sun | WE | On | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 9:00 | 8.9 | Sun | WE | On | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 10:00 | 9.3 | Sun | WE | On | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 11:00 | 9.5 | Sun | WE | On | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 12:00 | 9.3 | Sun | WE | On | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 13:00 | 9 | Sun | WE | On | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 14:00 | 8.7 | Sun | WE | On | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 15:00 | 8.6 | Sun | WE | On | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 16:00 | 9.2 | Sun | WE | On | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 17:00 | 9.4 | Sun | WE | On | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 18:00 | 9.5 | Sun | WE | On | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 19:00 | 9 | Sun | WE | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 20:00 | 8.3 | Sun | WE | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 21:00 | 8.2 | Sun | WE | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 22:00 | 7.7 | Sun | WE | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 23:00 | 7.2 | Sun | WE | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
Mon, 18/Apr | 24:00 | 6.8 | Mon | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 1:00 | 6.4 | Mon | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 2:00 | 6 | Mon | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 3:00 | 5.8 | Mon | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 4:00 | 5.6 | Mon | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 5:00 | 5.3 | Mon | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 6:00 | 5.2 | Mon | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 7:00 | 4.9 | Mon | School Day | On | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 8:00 | 4.4 | Mon | School Day | On | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 9:00 | 5.6 | Mon | School Day | On | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 10:00 | 6.6 | Mon | School Day | On | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 11:00 | 7.8 | Mon | School Day | On | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 12:00 | 8.7 | Mon | School Day | On | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 13:00 | 9.4 | Mon | School Day | On | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 14:00 | 11.6 | Mon | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 15:00 | 12.9 | Mon | School Day | On | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 16:00 | 13.3 | Mon | School Day | On | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 17:00 | 13.9 | Mon | School Day | On | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 18:00 | 14.3 | Mon | School Day | On | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 19:00 | 13.7 | Mon | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 20:00 | 13.1 | Mon | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 21:00 | 10.9 | Mon | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 22:00 | 10.3 | Mon | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 23:00 | 10 | Mon | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
Tue, 19/Apr | 24:00 | 9.9 | Tue | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 1:00 | 9.4 | Tue | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 2:00 | 7.5 | Tue | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 3:00 | 6.9 | Tue | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 4:00 | 6 | Tue | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 5:00 | 5.4 | Tue | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 6:00 | 4 | Tue | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 7:00 | 3.6 | Tue | School Day | On | Off | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 8:00 | 3.9 | Tue | School Day | On | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 9:00 | 5.4 | Tue | School Day | On | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 10:00 | 7.7 | Tue | School Day | On | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 11:00 | 10 | Tue | School Day | On | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 12:00 | 10.8 | Tue | School Day | On | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 13:00 | 11.6 | Tue | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 14:00 | 11.3 | Tue | School Day | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 15:00 | 11.7 | Tue | School Day | On | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 16:00 | 11.2 | Tue | School Day | On | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 17:00 | 11.9 | Tue | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 18:00 | 11.5 | Tue | School Day | On | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 19:00 | 11.3 | Tue | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 20:00 | 10.9 | Tue | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 21:00 | 10.7 | Tue | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 22:00 | 10.4 | Tue | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 23:00 | 10.1 | Tue | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
Wed, 20/Apr | 24:00 | 9.6 | Wed | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 1:00 | 9.6 | Wed | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 2:00 | 9 | Wed | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 3:00 | 9 | Wed | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 4:00 | 8.9 | Wed | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 5:00 | 8.3 | Wed | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 6:00 | 8.1 | Wed | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 7:00 | 8.2 | Wed | School Day | On | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 8:00 | 8.2 | Wed | School Day | On | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 9:00 | 8.4 | Wed | School Day | On | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 10:00 | 9.1 | Wed | School Day | On | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 11:00 | 9.5 | Wed | School Day | On | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 12:00 | 9.2 | Wed | School Day | On | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 13:00 | 8.6 | Wed | School Day | On | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 14:00 | 7.9 | Wed | School Day | On | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 15:00 | 9.3 | Wed | School Day | On | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 16:00 | 6.2 | Wed | School Day | On | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 17:00 | 9.4 | Wed | School Day | On | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 18:00 | 9.8 | Wed | School Day | On | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 19:00 | 8.4 | Wed | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 20:00 | 9 | Wed | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 21:00 | 8.3 | Wed | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 22:00 | 7.8 | Wed | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 23:00 | 7.7 | Wed | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
Thu, 21/Apr | 24:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 1:00 | 7.4 | Thu | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 2:00 | 6.9 | Thu | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 3:00 | 6.2 | Thu | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 4:00 | 6.1 | Thu | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 5:00 | 5.7 | Thu | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 6:00 | 5.3 | Thu | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 7:00 | 4.9 | Thu | School Day | On | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 8:00 | 4.4 | Thu | School Day | On | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 9:00 | 5.1 | Thu | School Day | On | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 10:00 | 6.9 | Thu | School Day | On | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 11:00 | 8.5 | Thu | School Day | On | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 12:00 | 9.4 | Thu | School Day | On | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 13:00 | 9.4 | Thu | School Day | On | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 14:00 | 9.5 | Thu | School Day | On | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 15:00 | 12 | Thu | School Day | On | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 16:00 | 11.4 | Thu | School Day | On | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 17:00 | 11.1 | Thu | School Day | On | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 18:00 | 11.6 | Thu | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 19:00 | 10 | Thu | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 20:00 | 10.7 | Thu | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 21:00 | 10.2 | Thu | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 22:00 | 9.1 | Thu | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 23:00 | 7.9 | Thu | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
Fri, 22/Apr | 24:00 | 6.9 | Fri | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 1:00 | 6.4 | Fri | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 2:00 | 5.8 | Fri | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 3:00 | 5.8 | Fri | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 4:00 | 4.7 | Fri | School Day | Off | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 5:00 | 4.9 | Fri | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 6:00 | 4 | Fri | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 7:00 | 5.5 | Fri | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 8:00 | 6.3 | Fri | School Day | On | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 9:00 | 7.2 | Fri | School Day | On | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 10:00 | 8.7 | Fri | School Day | On | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 11:00 | 9 | Fri | School Day | On | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 12:00 | 9.3 | Fri | School Day | On | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 13:00 | 9.8 | Fri | School Day | On | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 14:00 | 10.4 | Fri | School Day | On | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 15:00 | 11.3 | Fri | School Day | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 16:00 | 12.1 | Fri | School Day | On | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 17:00 | 12.7 | Fri | School Day | On | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 18:00 | 12.5 | Fri | School Day | On | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 19:00 | 12.5 | Fri | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 20:00 | 12.4 | Fri | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 21:00 | 11.5 | Fri | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 22:00 | 10.8 | Fri | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 23:00 | 9.5 | Fri | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
Sat, 23/Apr | 24:00 | 9.5 | Sat | WE | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 1:00 | 9.3 | Sat | WE | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 2:00 | 9.4 | Sat | WE | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 3:00 | 8.9 | Sat | WE | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 4:00 | 8.6 | Sat | WE | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 5:00 | 8.1 | Sat | WE | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 6:00 | 8.2 | Sat | WE | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 7:00 | 8.1 | Sat | WE | On | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 8:00 | 8.3 | Sat | WE | On | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 9:00 | 8.6 | Sat | WE | On | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 10:00 | 9.5 | Sat | WE | On | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 11:00 | 9.9 | Sat | WE | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 12:00 | 10.8 | Sat | WE | On | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 13:00 | 11.3 | Sat | WE | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 14:00 | 13.1 | Sat | WE | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 15:00 | 13.5 | Sat | WE | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 16:00 | 13.8 | Sat | WE | On | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 17:00 | 12.9 | Sat | WE | On | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 18:00 | 12.2 | Sat | WE | On | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 19:00 | 11 | Sat | WE | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 20:00 | 9.7 | Sat | WE | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 21:00 | 8.1 | Sat | WE | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 22:00 | 7.7 | Sat | WE | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 23:00 | 6.7 | Sat | WE | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
Sun, 24/Apr | 24:00 | 6.1 | Sun | WE | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 1:00 | 5.8 | Sun | WE | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 2:00 | 5.8 | Sun | WE | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 3:00 | 5.3 | Sun | WE | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 4:00 | 4.9 | Sun | WE | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 5:00 | 4.8 | Sun | WE | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 6:00 | 4.5 | Sun | WE | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 7:00 | 4.7 | Sun | WE | On | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 8:00 | 4.8 | Sun | WE | On | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 9:00 | 5.2 | Sun | WE | On | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 10:00 | 5.7 | Sun | WE | On | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 11:00 | 5.9 | Sun | WE | On | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 12:00 | 6.3 | Sun | WE | On | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 13:00 | 6.8 | Sun | WE | On | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 14:00 | 7.2 | Sun | WE | On | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 15:00 | 7.4 | Sun | WE | On | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 16:00 | 7 | Sun | WE | On | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 17:00 | 6.8 | Sun | WE | On | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 18:00 | 6.7 | Sun | WE | On | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 19:00 | 6.4 | Sun | WE | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 20:00 | 5.6 | Sun | WE | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 21:00 | 4.9 | Sun | WE | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 22:00 | 4.2 | Sun | WE | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 23:00 | 3.4 | Sun | WE | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
Mon, 25/Apr | 24:00 | 2.8 | Mon | School Day | Off | Off | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 1:00 | 2.9 | Mon | School Day | Off | Off | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 2:00 | 2.6 | Mon | School Day | Off | Off | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 0
| 3:00 | 2.5 | Mon | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 4:00 | 2.3 | Mon | School Day | Off | Off | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 0
| 5:00 | 2.3 | Mon | School Day | Off | Off | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 0
| 6:00 | 2.5 | Mon | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 7:00 | 2.6 | Mon | School Day | On | Off | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 0
| 8:00 | 2.6 | Mon | School Day | On | Off | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 0
| 9:00 | 3.7 | Mon | School Day | On | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 10:00 | 4.9 | Mon | School Day | On | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 11:00 | 5.4 | Mon | School Day | On | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 12:00 | 6 | Mon | School Day | On | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 13:00 | 7.2 | Mon | School Day | On | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 14:00 | 7.2 | Mon | School Day | On | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 15:00 | 7.7 | Mon | School Day | On | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 16:00 | 8.3 | Mon | School Day | On | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 17:00 | 7.5 | Mon | School Day | On | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 18:00 | 7.6 | Mon | School Day | On | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 19:00 | 6.6 | Mon | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 20:00 | 5.9 | Mon | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 21:00 | 5.6 | Mon | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 22:00 | 5.4 | Mon | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 23:00 | 5.2 | Mon | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
Tue, 26/Apr | 24:00 | 4.2 | Tue | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 1:00 | 3.4 | Tue | School Day | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 2:00 | 2.7 | Tue | School Day | Off | Off | 22 | 20.07 | 1.93 | 1.7 | 3.6865 | 0.25 | 1035 | 1.6451 | 0
| 3:00 | 1.5 | Tue | School Day | Off | Off | 22 | 19.95 | 2.05 | 1.7 | 3.9157 | 0.25 | 1035 | 1.7473 | 0
| 4:00 | 1.3 | Tue | School Day | Off | Off | 22 | 19.93 | 2.07 | 1.7 | 3.9539 | 0.25 | 1035 | 1.7644 | 0
| 5:00 | 1.1 | Tue | School Day | Off | Off | 22 | 19.91 | 2.09 | 1.7 | 3.9921 | 0.25 | 1035 | 1.7814 | 0
| 6:00 | 0.9 | Tue | School Day | Off | Off | 22 | 19.89 | 2.11 | 1.7 | 4.0303 | 0.25 | 1035 | 1.7985 | 0
| 7:00 | 0.7 | Tue | School Day | On | Off | 22 | 19.87 | 2.13 | 1.7 | 4.0685 | 0.25 | 1035 | 1.8155 | 0
| 8:00 | 1.4 | Tue | School Day | On | Off | 22 | 19.94 | 2.06 | 1.7 | 3.9348 | 0.25 | 1035 | 1.7559 | 0
| 9:00 | 2.8 | Tue | School Day | On | Off | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 10:00 | 5.5 | Tue | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 11:00 | 7.5 | Tue | School Day | On | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 12:00 | 8.8 | Tue | School Day | On | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 13:00 | 9.7 | Tue | School Day | On | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 14:00 | 10.6 | Tue | School Day | On | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 15:00 | 10.8 | Tue | School Day | On | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 16:00 | 11.3 | Tue | School Day | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 17:00 | 11.5 | Tue | School Day | On | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 18:00 | 12.2 | Tue | School Day | On | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 19:00 | 10.8 | Tue | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 20:00 | 9.8 | Tue | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 21:00 | 9 | Tue | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 22:00 | 8.3 | Tue | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 23:00 | 8 | Tue | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
Wed, 27/Apr | 24:00 | 8 | Wed | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 1:00 | 7.9 | Wed | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 2:00 | 7.7 | Wed | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 3:00 | 7.5 | Wed | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 4:00 | 6.6 | Wed | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 5:00 | 6.4 | Wed | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 6:00 | 5.8 | Wed | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 7:00 | 5.7 | Wed | School Day | On | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 8:00 | 6 | Wed | School Day | On | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 9:00 | 6.6 | Wed | School Day | On | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 10:00 | 7.1 | Wed | School Day | On | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 11:00 | 7.8 | Wed | School Day | On | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 12:00 | 8.2 | Wed | School Day | On | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 13:00 | 9 | Wed | School Day | On | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 14:00 | 8.1 | Wed | School Day | On | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 15:00 | 8.7 | Wed | School Day | On | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 16:00 | 8.6 | Wed | School Day | On | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 17:00 | 7.7 | Wed | School Day | On | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 18:00 | 7.8 | Wed | School Day | On | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 19:00 | 6.7 | Wed | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 20:00 | 7.4 | Wed | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 21:00 | 8 | Wed | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 22:00 | 7.3 | Wed | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 23:00 | 7.4 | Wed | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
Thu, 28/Apr | 24:00 | 6.8 | Thu | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 1:00 | 6.7 | Thu | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 2:00 | 6.4 | Thu | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 3:00 | 6.1 | Thu | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 4:00 | 4.7 | Thu | School Day | Off | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 5:00 | 3.8 | Thu | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 6:00 | 3.2 | Thu | School Day | Off | Off | 22 | 20.12 | 1.88 | 1.7 | 3.591 | 0.25 | 1035 | 1.6024 | 0
| 7:00 | 2.8 | Thu | School Day | On | Off | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 8:00 | 3.8 | Thu | School Day | On | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 9:00 | 5.6 | Thu | School Day | On | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 10:00 | 7.9 | Thu | School Day | On | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 11:00 | 9.3 | Thu | School Day | On | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 12:00 | 10.7 | Thu | School Day | On | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 13:00 | 12.1 | Thu | School Day | On | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 14:00 | 12.3 | Thu | School Day | On | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 15:00 | 12.9 | Thu | School Day | On | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 16:00 | 14.1 | Thu | School Day | On | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 17:00 | 14.3 | Thu | School Day | On | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 18:00 | 13.8 | Thu | School Day | On | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 19:00 | 14 | Thu | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 20:00 | 13.8 | Thu | School Day | Off | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 21:00 | 11.9 | Thu | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 22:00 | 11.8 | Thu | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 23:00 | 10.5 | Thu | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
Fri, 29/Apr | 24:00 | 9.5 | Fri | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 1:00 | 9.4 | Fri | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 2:00 | 8.9 | Fri | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 3:00 | 8.6 | Fri | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 4:00 | 8.1 | Fri | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 5:00 | 8.1 | Fri | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 6:00 | 8.2 | Fri | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 7:00 | 7.8 | Fri | School Day | On | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 8:00 | 7.6 | Fri | School Day | On | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 9:00 | 7.6 | Fri | School Day | On | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 10:00 | 7.8 | Fri | School Day | On | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 11:00 | 7.8 | Fri | School Day | On | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 12:00 | 8.1 | Fri | School Day | On | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 13:00 | 8.2 | Fri | School Day | On | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 14:00 | 8.9 | Fri | School Day | On | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 15:00 | 9.1 | Fri | School Day | On | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 16:00 | 9.6 | Fri | School Day | On | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 17:00 | 9.6 | Fri | School Day | On | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 18:00 | 9.7 | Fri | School Day | On | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 19:00 | 9.9 | Fri | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 20:00 | 9.7 | Fri | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 21:00 | 9.7 | Fri | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 22:00 | 9.1 | Fri | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 23:00 | 9.1 | Fri | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
Sat, 30/Apr | 24:00 | 8.7 | Sat | WE | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 1:00 | 8.3 | Sat | WE | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 2:00 | 7.9 | Sat | WE | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 3:00 | 7.6 | Sat | WE | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 4:00 | 7.6 | Sat | WE | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 5:00 | 6.9 | Sat | WE | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 6:00 | 7.3 | Sat | WE | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 7:00 | 7.3 | Sat | WE | On | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 8:00 | 7.9 | Sat | WE | On | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 9:00 | 8.7 | Sat | WE | On | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 10:00 | 10.2 | Sat | WE | On | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 11:00 | 11 | Sat | WE | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 12:00 | 12.4 | Sat | WE | On | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 13:00 | 14 | Sat | WE | On | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 14:00 | 13.7 | Sat | WE | On | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 15:00 | 14.4 | Sat | WE | On | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 16:00 | 14.7 | Sat | WE | On | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 17:00 | 14.9 | Sat | WE | On | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 18:00 | 14.7 | Sat | WE | On | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 19:00 | 14.1 | Sat | WE | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 20:00 | 13.5 | Sat | WE | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 21:00 | 12.9 | Sat | WE | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 22:00 | 12.2 | Sat | WE | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 23:00 | 11.6 | Sat | WE | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
Sun, 01/May | 24:00 | 11.2 | Sun | WE | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 1:00 | 10.9 | Sun | WE | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 2:00 | 10.4 | Sun | WE | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 3:00 | 10.5 | Sun | WE | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 4:00 | 10.6 | Sun | WE | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 5:00 | 10.4 | Sun | WE | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 6:00 | 10.5 | Sun | WE | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 7:00 | 10.8 | Sun | WE | On | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 8:00 | 11.1 | Sun | WE | On | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 9:00 | 11.9 | Sun | WE | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 10:00 | 12.6 | Sun | WE | On | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 11:00 | 13.7 | Sun | WE | On | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 12:00 | 14.5 | Sun | WE | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 13:00 | 15.2 | Sun | WE | On | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 14:00 | 16.1 | Sun | WE | On | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 15:00 | 16.5 | Sun | WE | On | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 16:00 | 16.2 | Sun | WE | On | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 17:00 | 16.4 | Sun | WE | On | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 18:00 | 16.9 | Sun | WE | On | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 19:00 | 17.1 | Sun | WE | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 20:00 | 16.9 | Sun | WE | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 21:00 | 16.5 | Sun | WE | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 22:00 | 15.7 | Sun | WE | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 23:00 | 13.2 | Sun | WE | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
Mon, 02/May | 24:00 | 13.3 | Mon | School Day | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 1:00 | 13.9 | Mon | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 2:00 | 12.9 | Mon | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 3:00 | 11.7 | Mon | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 4:00 | 11.2 | Mon | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 5:00 | 10.9 | Mon | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 6:00 | 10.9 | Mon | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 7:00 | 11 | Mon | School Day | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 8:00 | 11.1 | Mon | School Day | On | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 9:00 | 11.8 | Mon | School Day | On | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 10:00 | 13.5 | Mon | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 11:00 | 14.5 | Mon | School Day | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 12:00 | 15.6 | Mon | School Day | On | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 13:00 | 17.1 | Mon | School Day | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 14:00 | 18.1 | Mon | School Day | On | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 15:00 | 19.8 | Mon | School Day | On | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 16:00 | 20.8 | Mon | School Day | On | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 17:00 | 21 | Mon | School Day | On | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 18:00 | 21.3 | Mon | School Day | On | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 19:00 | 20.7 | Mon | School Day | Off | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 20:00 | 19.8 | Mon | School Day | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 21:00 | 19.5 | Mon | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 22:00 | 17.6 | Mon | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 23:00 | 16.8 | Mon | School Day | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
Tue, 03/May | 24:00 | 15.1 | Tue | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 1:00 | 13.9 | Tue | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 2:00 | 13 | Tue | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 3:00 | 12.1 | Tue | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 4:00 | 11.4 | Tue | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 5:00 | 10.8 | Tue | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 6:00 | 9.6 | Tue | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 7:00 | 9.3 | Tue | School Day | On | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 8:00 | 10.1 | Tue | School Day | On | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 9:00 | 12.1 | Tue | School Day | On | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 10:00 | 14.1 | Tue | School Day | On | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 11:00 | 16.5 | Tue | School Day | On | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 12:00 | 18.8 | Tue | School Day | On | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 13:00 | 20.3 | Tue | School Day | On | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 14:00 | 22 | Tue | School Day | On | Off | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 22.1 | Tue | School Day | On | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 22.5 | Tue | School Day | On | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23.8 | Tue | School Day | On | Off | 22 | 22.18 | -0.18 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 23.4 | Tue | School Day | On | Off | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.9 | Tue | School Day | Off | Off | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 21.6 | Tue | School Day | Off | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 21:00 | 20 | Tue | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 22:00 | 17.7 | Tue | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 23:00 | 16.7 | Tue | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
Wed, 04/May | 24:00 | 15.6 | Wed | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 1:00 | 14.4 | Wed | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 2:00 | 14.4 | Wed | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 3:00 | 13.7 | Wed | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 4:00 | 12.8 | Wed | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 5:00 | 11.8 | Wed | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 6:00 | 11 | Wed | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 7:00 | 10.3 | Wed | School Day | On | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 8:00 | 10.6 | Wed | School Day | On | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 9:00 | 11.9 | Wed | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 10:00 | 14.2 | Wed | School Day | On | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 11:00 | 17.1 | Wed | School Day | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 12:00 | 19.2 | Wed | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 13:00 | 21.2 | Wed | School Day | On | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 14:00 | 22.6 | Wed | School Day | On | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.5 | Wed | School Day | On | Off | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 24.1 | Wed | School Day | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 24.5 | Wed | School Day | On | Off | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 24 | Wed | School Day | On | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 23.1 | Wed | School Day | Off | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 21.7 | Wed | School Day | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 21:00 | 19.7 | Wed | School Day | Off | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 22:00 | 17.1 | Wed | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 23:00 | 15.2 | Wed | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
Thu, 05/May | 24:00 | 14.9 | Thu | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 1:00 | 13.9 | Thu | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 2:00 | 13.9 | Thu | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 3:00 | 13.6 | Thu | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 4:00 | 12.7 | Thu | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 5:00 | 12 | Thu | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 6:00 | 11.3 | Thu | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 7:00 | 10.9 | Thu | School Day | On | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 8:00 | 11.4 | Thu | School Day | On | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 9:00 | 13.6 | Thu | School Day | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 10:00 | 15.5 | Thu | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 11:00 | 18.1 | Thu | School Day | On | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 12:00 | 20.6 | Thu | School Day | On | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 13:00 | 22.6 | Thu | School Day | On | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 23.6 | Thu | School Day | On | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 24.4 | Thu | School Day | On | Off | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 25.4 | Thu | School Day | On | Off | 22 | 22.34 | -0.34 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.9 | Thu | School Day | On | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.8 | Thu | School Day | On | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.3 | Thu | School Day | Off | Off | 22 | 22.33 | -0.33 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 23.9 | Thu | School Day | Off | Off | 22 | 22.19 | -0.19 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 22.5 | Thu | School Day | Off | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 21.1 | Thu | School Day | Off | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 23:00 | 19.2 | Thu | School Day | Off | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
Fri, 06/May | 24:00 | 16.6 | Fri | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 1:00 | 15 | Fri | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 2:00 | 13.5 | Fri | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 3:00 | 13.1 | Fri | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 4:00 | 12.7 | Fri | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 5:00 | 11.9 | Fri | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 6:00 | 11.4 | Fri | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 7:00 | 11 | Fri | School Day | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 8:00 | 11 | Fri | School Day | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 9:00 | 11.2 | Fri | School Day | On | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 10:00 | 12.3 | Fri | School Day | On | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 11:00 | 14.3 | Fri | School Day | On | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 12:00 | 15.3 | Fri | School Day | On | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 13:00 | 16.1 | Fri | School Day | On | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 14:00 | 16.6 | Fri | School Day | On | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 15:00 | 16.9 | Fri | School Day | On | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 16:00 | 17.4 | Fri | School Day | On | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 17:00 | 17.4 | Fri | School Day | On | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 18:00 | 17.6 | Fri | School Day | On | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 19:00 | 16.9 | Fri | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 20:00 | 16.3 | Fri | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 21:00 | 16 | Fri | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 22:00 | 14.1 | Fri | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 23:00 | 12.6 | Fri | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
Sat, 07/May | 24:00 | 10 | Sat | WE | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 1:00 | 9.4 | Sat | WE | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 2:00 | 8.6 | Sat | WE | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 3:00 | 7.4 | Sat | WE | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 4:00 | 8.1 | Sat | WE | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 5:00 | 7 | Sat | WE | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 6:00 | 6.8 | Sat | WE | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 7:00 | 7.2 | Sat | WE | On | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 8:00 | 8.1 | Sat | WE | On | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 9:00 | 9.6 | Sat | WE | On | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 10:00 | 11 | Sat | WE | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 11:00 | 12.6 | Sat | WE | On | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 12:00 | 14.5 | Sat | WE | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 13:00 | 15.7 | Sat | WE | On | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 14:00 | 17.1 | Sat | WE | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 15:00 | 18.5 | Sat | WE | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 16:00 | 19 | Sat | WE | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 17:00 | 19.1 | Sat | WE | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 18:00 | 19.5 | Sat | WE | On | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 19:00 | 19.9 | Sat | WE | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 20:00 | 18.9 | Sat | WE | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 21:00 | 18.8 | Sat | WE | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 22:00 | 16.6 | Sat | WE | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 23:00 | 14.6 | Sat | WE | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
Sun, 08/May | 24:00 | 12.9 | Sun | WE | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 1:00 | 12.2 | Sun | WE | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 2:00 | 11.4 | Sun | WE | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 3:00 | 10.6 | Sun | WE | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 4:00 | 9.8 | Sun | WE | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 5:00 | 9.2 | Sun | WE | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 6:00 | 8.9 | Sun | WE | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 7:00 | 8.1 | Sun | WE | On | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 8:00 | 9 | Sun | WE | On | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 9:00 | 11 | Sun | WE | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 10:00 | 13.3 | Sun | WE | On | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 11:00 | 15.9 | Sun | WE | On | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 12:00 | 17.8 | Sun | WE | On | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 13:00 | 19.6 | Sun | WE | On | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 14:00 | 20.7 | Sun | WE | On | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 15:00 | 21.5 | Sun | WE | On | Off | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 16:00 | 22.4 | Sun | WE | On | Off | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 22.8 | Sun | WE | On | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.2 | Sun | WE | On | Off | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.1 | Sun | WE | Off | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 21.3 | Sun | WE | Off | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 21:00 | 20.4 | Sun | WE | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 22:00 | 19.1 | Sun | WE | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 23:00 | 17.9 | Sun | WE | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
Mon, 09/May | 24:00 | 16.7 | Mon | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 1:00 | 15.7 | Mon | School Day | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 2:00 | 14.3 | Mon | School Day | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 3:00 | 12.2 | Mon | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 4:00 | 11.9 | Mon | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 5:00 | 11.4 | Mon | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 6:00 | 9.8 | Mon | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 7:00 | 10 | Mon | School Day | On | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 8:00 | 10.9 | Mon | School Day | On | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 9:00 | 12.2 | Mon | School Day | On | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 10:00 | 15.1 | Mon | School Day | On | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 11:00 | 17.9 | Mon | School Day | On | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 12:00 | 19.5 | Mon | School Day | On | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 13:00 | 20.1 | Mon | School Day | On | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 14:00 | 20.5 | Mon | School Day | On | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 15:00 | 19.6 | Mon | School Day | On | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 16:00 | 19 | Mon | School Day | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 17:00 | 19.5 | Mon | School Day | On | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 18:00 | 19 | Mon | School Day | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 19:00 | 18.9 | Mon | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 20:00 | 17.9 | Mon | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 21:00 | 16.6 | Mon | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 22:00 | 15.2 | Mon | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 23:00 | 14.6 | Mon | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
Tue, 10/May | 24:00 | 13.8 | Tue | School Day | Off | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 1:00 | 13.7 | Tue | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 2:00 | 13.1 | Tue | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 3:00 | 12.2 | Tue | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 4:00 | 11.4 | Tue | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 5:00 | 10.4 | Tue | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 6:00 | 9.3 | Tue | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 7:00 | 8.1 | Tue | School Day | On | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 8:00 | 8.8 | Tue | School Day | On | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 9:00 | 10.3 | Tue | School Day | On | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 10:00 | 12.5 | Tue | School Day | On | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 11:00 | 13.7 | Tue | School Day | On | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 12:00 | 15.5 | Tue | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 13:00 | 16 | Tue | School Day | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 14:00 | 17.1 | Tue | School Day | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 15:00 | 17 | Tue | School Day | On | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 16:00 | 18 | Tue | School Day | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 17:00 | 17.7 | Tue | School Day | On | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 18:00 | 18.3 | Tue | School Day | On | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 19:00 | 17.8 | Tue | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 20:00 | 17.3 | Tue | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 21:00 | 17 | Tue | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 22:00 | 16.1 | Tue | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 23:00 | 15.7 | Tue | School Day | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
Wed, 11/May | 24:00 | 14.1 | Wed | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 1:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 2:00 | 13.6 | Wed | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 3:00 | 12.7 | Wed | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 4:00 | 12.9 | Wed | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 5:00 | 12.1 | Wed | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 6:00 | 11.6 | Wed | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 7:00 | 11.9 | Wed | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 8:00 | 12.1 | Wed | School Day | On | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 9:00 | 12.8 | Wed | School Day | On | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 10:00 | 13.6 | Wed | School Day | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 11:00 | 14.7 | Wed | School Day | On | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 12:00 | 16.1 | Wed | School Day | On | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 13:00 | 16.7 | Wed | School Day | On | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 14:00 | 18.2 | Wed | School Day | On | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 15:00 | 18.5 | Wed | School Day | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 16:00 | 15.5 | Wed | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 17:00 | 16 | Wed | School Day | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 18:00 | 15.3 | Wed | School Day | On | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 19:00 | 14.7 | Wed | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 20:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 21:00 | 13.4 | Wed | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 22:00 | 12.9 | Wed | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 23:00 | 10.1 | Wed | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
Thu, 12/May | 24:00 | 10 | Thu | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 1:00 | 9.2 | Thu | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 2:00 | 8.8 | Thu | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 3:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 4:00 | 7.8 | Thu | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 5:00 | 8 | Thu | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 6:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 7:00 | 8 | Thu | School Day | On | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 8:00 | 8.3 | Thu | School Day | On | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 9:00 | 9.2 | Thu | School Day | On | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 10:00 | 9.9 | Thu | School Day | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 11:00 | 12.1 | Thu | School Day | On | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 12:00 | 12 | Thu | School Day | On | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 13:00 | 12.6 | Thu | School Day | On | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 14:00 | 13.3 | Thu | School Day | On | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 15:00 | 14.7 | Thu | School Day | On | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 16:00 | 13.1 | Thu | School Day | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 17:00 | 13 | Thu | School Day | On | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 18:00 | 13.2 | Thu | School Day | On | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 19:00 | 13.1 | Thu | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 20:00 | 13.2 | Thu | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 21:00 | 12.3 | Thu | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 22:00 | 12.1 | Thu | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 23:00 | 11 | Thu | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
Fri, 13/May | 24:00 | 10.4 | Fri | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 1:00 | 9.7 | Fri | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 2:00 | 9.2 | Fri | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 3:00 | 9.4 | Fri | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 4:00 | 8.6 | Fri | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 5:00 | 7.9 | Fri | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 6:00 | 7.4 | Fri | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 7:00 | 7.4 | Fri | School Day | On | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 8:00 | 8.6 | Fri | School Day | On | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 9:00 | 9 | Fri | School Day | On | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 10:00 | 11.6 | Fri | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 11:00 | 13.5 | Fri | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 12:00 | 13.4 | Fri | School Day | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 13:00 | 13.6 | Fri | School Day | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 14:00 | 14.4 | Fri | School Day | On | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 15:00 | 15.2 | Fri | School Day | On | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 16:00 | 15.7 | Fri | School Day | On | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 17:00 | 15.7 | Fri | School Day | On | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 18:00 | 15.3 | Fri | School Day | On | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 19:00 | 15.3 | Fri | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 20:00 | 15.4 | Fri | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 21:00 | 14.5 | Fri | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 22:00 | 13.1 | Fri | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 23:00 | 12.1 | Fri | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
Sat, 14/May | 24:00 | 11.4 | Sat | WE | Off | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 1:00 | 11.4 | Sat | WE | Off | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 2:00 | 11.4 | Sat | WE | Off | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 3:00 | 11 | Sat | WE | Off | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 4:00 | 11 | Sat | WE | Off | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 5:00 | 10.8 | Sat | WE | Off | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 6:00 | 10.8 | Sat | WE | Off | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 7:00 | 10.8 | Sat | WE | On | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 8:00 | 11.6 | Sat | WE | On | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 9:00 | 12.3 | Sat | WE | On | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 10:00 | 14.1 | Sat | WE | On | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 11:00 | 15.4 | Sat | WE | On | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 12:00 | 16.1 | Sat | WE | On | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 13:00 | 17.5 | Sat | WE | On | OFF | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 14:00 | 18.2 | Sat | WE | On | OFF | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 15:00 | 17.7 | Sat | WE | On | OFF | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 16:00 | 17.6 | Sat | WE | On | OFF | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 17:00 | 17.3 | Sat | WE | On | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 18:00 | 17.8 | Sat | WE | On | OFF | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 19:00 | 16.9 | Sat | WE | Off | OFF | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 20:00 | 16 | Sat | WE | Off | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 21:00 | 15.9 | Sat | WE | Off | OFF | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 22:00 | 15.7 | Sat | WE | Off | OFF | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 23:00 | 15.1 | Sat | WE | Off | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
Sun, 15/May | 24:00 | 14.6 | Sun | WE | Off | OFF | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 1:00 | 13.4 | Sun | WE | Off | OFF | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 2:00 | 12 | Sun | WE | Off | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 3:00 | 10.9 | Sun | WE | Off | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 4:00 | 10.1 | Sun | WE | Off | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 5:00 | 9.1 | Sun | WE | Off | OFF | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 6:00 | 10 | Sun | WE | Off | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 7:00 | 10.7 | Sun | WE | On | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 8:00 | 11.6 | Sun | WE | On | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 9:00 | 12.5 | Sun | WE | On | OFF | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 10:00 | 14.6 | Sun | WE | On | OFF | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 11:00 | 16.4 | Sun | WE | On | OFF | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 12:00 | 17.8 | Sun | WE | On | OFF | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 13:00 | 18.9 | Sun | WE | On | OFF | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 14:00 | 19.1 | Sun | WE | On | OFF | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 15:00 | 20.8 | Sun | WE | On | OFF | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 16:00 | 21.8 | Sun | WE | On | OFF | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0
| 17:00 | 21.1 | Sun | WE | On | OFF | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 18:00 | 20.9 | Sun | WE | On | OFF | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 19:00 | 20.8 | Sun | WE | Off | OFF | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 20:00 | 19.9 | Sun | WE | Off | OFF | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 21:00 | 18.7 | Sun | WE | Off | OFF | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 22:00 | 17.2 | Sun | WE | Off | OFF | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 23:00 | 16.1 | Sun | WE | Off | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
Mon, 16/May | 24:00 | 14.7 | Mon | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 1:00 | 13.6 | Mon | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 2:00 | 13 | Mon | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 3:00 | 12.2 | Mon | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 4:00 | 12.3 | Mon | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 5:00 | 12.3 | Mon | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 6:00 | 11.6 | Mon | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 7:00 | 11 | Mon | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 8:00 | 11.8 | Mon | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 9:00 | 13 | Mon | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 10:00 | 15.5 | Mon | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 11:00 | 17.1 | Mon | School Day | On | On | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 1.3536
| 12:00 | 18.7 | Mon | School Day | On | On | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0.91161
| 13:00 | 19.8 | Mon | School Day | On | On | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0.60774
| 14:00 | 20.7 | Mon | School Day | On | On | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0.35912
| 15:00 | 21.2 | Mon | School Day | On | On | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0.221
| 16:00 | 21.4 | Mon | School Day | On | On | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0.16575
| 17:00 | 20.7 | Mon | School Day | On | On | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0.35912
| 18:00 | 19.5 | Mon | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 19:00 | 20.9 | Mon | School Day | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 20:00 | 20.5 | Mon | School Day | Off | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 21:00 | 19.5 | Mon | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 22:00 | 18.5 | Mon | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 23:00 | 17.5 | Mon | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
Tue, 17/May | 24:00 | 16.7 | Tue | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 1:00 | 15.4 | Tue | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 2:00 | 14.6 | Tue | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 3:00 | 13.8 | Tue | School Day | Off | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 4:00 | 12.3 | Tue | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 5:00 | 13.1 | Tue | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 6:00 | 12.3 | Tue | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 7:00 | 12.3 | Tue | School Day | On | On | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 2.6796
| 8:00 | 13 | Tue | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 9:00 | 14.4 | Tue | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 10:00 | 15.6 | Tue | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 11:00 | 18.3 | Tue | School Day | On | On | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 1.0221
| 12:00 | 19.3 | Tue | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 13:00 | 19.2 | Tue | School Day | On | On | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0.77349
| 14:00 | 21.5 | Tue | School Day | On | On | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0.13812
| 15:00 | 21.8 | Tue | School Day | On | On | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0.055249
| 16:00 | 22.1 | Tue | School Day | On | On | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 22.2 | Tue | School Day | On | On | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 21.7 | Tue | School Day | On | On | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0.082874
| 19:00 | 22.3 | Tue | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 22.3 | Tue | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.6 | Tue | School Day | Off | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 22:00 | 20.8 | Tue | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 23:00 | 19.9 | Tue | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
Wed, 18/May | 24:00 | 17.6 | Wed | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 1:00 | 16.8 | Wed | School Day | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 2:00 | 15.8 | Wed | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 3:00 | 15.3 | Wed | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 4:00 | 13.4 | Wed | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 5:00 | 13.1 | Wed | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 6:00 | 12.9 | Wed | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 7:00 | 12.8 | Wed | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 8:00 | 13.5 | Wed | School Day | On | On | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 2.3481
| 9:00 | 15.7 | Wed | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 10:00 | 17.6 | Wed | School Day | On | On | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 1.2155
| 11:00 | 19.8 | Wed | School Day | On | On | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0.60774
| 12:00 | 21.7 | Wed | School Day | On | On | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0.082874
| 13:00 | 21.6 | Wed | School Day | On | On | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0.1105
| 14:00 | 22.7 | Wed | School Day | On | On | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.1 | Wed | School Day | On | On | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 24.2 | Wed | School Day | On | On | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 24.4 | Wed | School Day | On | On | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 24.4 | Wed | School Day | On | On | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 24.8 | Wed | School Day | Off | Off | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 23.2 | Wed | School Day | Off | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 22 | Wed | School Day | Off | Off | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 20.4 | Wed | School Day | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 23:00 | 19.1 | Wed | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
Thu, 19/May | 24:00 | 19.1 | Thu | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 1:00 | 18.7 | Thu | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 2:00 | 18.5 | Thu | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 3:00 | 16.6 | Thu | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 4:00 | 15.3 | Thu | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 5:00 | 14.6 | Thu | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 6:00 | 13.5 | Thu | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 7:00 | 13.6 | Thu | School Day | On | On | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 2.3205
| 8:00 | 14.6 | Thu | School Day | On | On | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 2.0442
| 9:00 | 16.6 | Thu | School Day | On | On | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 1.4917
| 10:00 | 19.3 | Thu | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 11:00 | 21.1 | Thu | School Day | On | On | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0.24862
| 12:00 | 22.8 | Thu | School Day | On | On | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 24.2 | Thu | School Day | On | On | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 23.3 | Thu | School Day | On | On | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.9 | Thu | School Day | On | On | 22 | 22.19 | -0.19 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 24.8 | Thu | School Day | On | On | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.2 | Thu | School Day | On | On | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25 | Thu | School Day | On | On | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 24.2 | Thu | School Day | Off | Off | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 23.1 | Thu | School Day | Off | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.7 | Thu | School Day | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 22:00 | 20.5 | Thu | School Day | Off | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 23:00 | 20.2 | Thu | School Day | Off | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
Fri, 20/May | 24:00 | 19.1 | Fri | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 1:00 | 17.6 | Fri | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 2:00 | 16.7 | Fri | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 3:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 4:00 | 14.7 | Fri | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 5:00 | 13.9 | Fri | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 6:00 | 13.3 | Fri | School Day | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 7:00 | 12.8 | Fri | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 8:00 | 13.1 | Fri | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 9:00 | 14.2 | Fri | School Day | On | On | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 2.1547
| 10:00 | 15.8 | Fri | School Day | On | On | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 1.7127
| 11:00 | 17.1 | Fri | School Day | On | On | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 1.3536
| 12:00 | 19.3 | Fri | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 13:00 | 22.3 | Fri | School Day | On | On | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 23.5 | Fri | School Day | On | On | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 25 | Fri | School Day | On | On | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26 | Fri | School Day | On | On | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26 | Fri | School Day | On | On | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.4 | Fri | School Day | On | On | 22 | 22.34 | -0.34 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 24.3 | Fri | School Day | Off | Off | 22 | 22.23 | -0.23 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 23.2 | Fri | School Day | Off | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 22.3 | Fri | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 20.8 | Fri | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 23:00 | 19.9 | Fri | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
Sat, 21/May | 24:00 | 18.9 | Sat | WE | Off | OFF | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 1:00 | 18.2 | Sat | WE | Off | OFF | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 2:00 | 17.1 | Sat | WE | Off | OFF | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 3:00 | 16.5 | Sat | WE | Off | OFF | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 4:00 | 15.9 | Sat | WE | Off | OFF | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 5:00 | 15 | Sat | WE | Off | OFF | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 6:00 | 14.5 | Sat | WE | Off | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 7:00 | 14.2 | Sat | WE | On | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 8:00 | 15.1 | Sat | WE | On | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 9:00 | 17 | Sat | WE | On | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 10:00 | 18.9 | Sat | WE | On | OFF | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 11:00 | 21.5 | Sat | WE | On | OFF | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 12:00 | 24.1 | Sat | WE | On | OFF | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 25.7 | Sat | WE | On | OFF | 22 | 22.37 | -0.37 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 26.4 | Sat | WE | On | OFF | 22 | 22.44 | -0.44 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27.1 | Sat | WE | On | OFF | 22 | 22.51 | -0.51 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27 | Sat | WE | On | OFF | 22 | 22.5 | -0.5 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.3 | Sat | WE | On | OFF | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.9 | Sat | WE | On | OFF | 22 | 22.49 | -0.49 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.7 | Sat | WE | Off | OFF | 22 | 22.37 | -0.37 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.6 | Sat | WE | Off | OFF | 22 | 22.26 | -0.26 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.6 | Sat | WE | Off | OFF | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.7 | Sat | WE | Off | OFF | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.7 | Sat | WE | Off | OFF | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
Sun, 22/May | 24:00 | 21.1 | Sun | WE | Off | OFF | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 1:00 | 20 | Sun | WE | Off | OFF | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 2:00 | 18.7 | Sun | WE | Off | OFF | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 3:00 | 18 | Sun | WE | Off | OFF | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 4:00 | 17.3 | Sun | WE | Off | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 5:00 | 17 | Sun | WE | Off | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 6:00 | 16.4 | Sun | WE | Off | OFF | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 7:00 | 16.4 | Sun | WE | On | OFF | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 8:00 | 16.9 | Sun | WE | On | OFF | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 9:00 | 17.8 | Sun | WE | On | OFF | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 10:00 | 19 | Sun | WE | On | OFF | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 11:00 | 22.1 | Sun | WE | On | OFF | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 23.9 | Sun | WE | On | OFF | 22 | 22.19 | -0.19 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 24.7 | Sun | WE | On | OFF | 22 | 22.27 | -0.27 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 26.1 | Sun | WE | On | OFF | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26.6 | Sun | WE | On | OFF | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26.6 | Sun | WE | On | OFF | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26.5 | Sun | WE | On | OFF | 22 | 22.45 | -0.45 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 24.5 | Sun | WE | On | OFF | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 24.2 | Sun | WE | Off | OFF | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24 | Sun | WE | Off | OFF | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.1 | Sun | WE | Off | OFF | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.2 | Sun | WE | Off | OFF | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.1 | Sun | WE | Off | OFF | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
Mon, 23/May | 24:00 | 20.1 | Mon | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 1:00 | 18.9 | Mon | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 2:00 | 18.1 | Mon | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 3:00 | 17.7 | Mon | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 4:00 | 17 | Mon | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 5:00 | 16.8 | Mon | School Day | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 6:00 | 16.8 | Mon | School Day | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 7:00 | 17 | Mon | School Day | On | On | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 1.3812
| 8:00 | 18 | Mon | School Day | On | On | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 1.105
| 9:00 | 19.7 | Mon | School Day | On | On | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0.63537
| 10:00 | 20.9 | Mon | School Day | On | On | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0.30387
| 11:00 | 23.2 | Mon | School Day | On | On | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25.7 | Mon | School Day | On | On | 22 | 22.37 | -0.37 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 27.3 | Mon | School Day | On | On | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 28.7 | Mon | School Day | On | On | 22 | 22.67 | -0.67 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 29.1 | Mon | School Day | On | On | 22 | 22.71 | -0.71 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 29 | Mon | School Day | On | On | 22 | 22.7 | -0.7 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 29.7 | Mon | School Day | On | On | 22 | 22.77 | -0.77 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 29.5 | Mon | School Day | On | On | 22 | 22.75 | -0.75 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 29.2 | Mon | School Day | Off | Off | 22 | 22.72 | -0.72 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 28.3 | Mon | School Day | Off | Off | 22 | 22.63 | -0.63 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 27.6 | Mon | School Day | Off | Off | 22 | 22.56 | -0.56 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 26.5 | Mon | School Day | Off | Off | 22 | 22.45 | -0.45 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 25.5 | Mon | School Day | Off | Off | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Tue, 24/May | 24:00 | 24.4 | Tue | School Day | Off | Off | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 23.1 | Tue | School Day | Off | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 2:00 | 21.7 | Tue | School Day | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 3:00 | 20.7 | Tue | School Day | Off | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 4:00 | 19.5 | Tue | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 5:00 | 19.5 | Tue | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 6:00 | 18.7 | Tue | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 7:00 | 18.5 | Tue | School Day | On | On | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0.96686
| 8:00 | 19.5 | Tue | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 9:00 | 20.7 | Tue | School Day | On | On | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0.35912
| 10:00 | 23.3 | Tue | School Day | On | On | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 11:00 | 25.5 | Tue | School Day | On | On | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 27.6 | Tue | School Day | On | On | 22 | 22.56 | -0.56 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 28.9 | Tue | School Day | On | On | 22 | 22.69 | -0.69 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 27.4 | Tue | School Day | On | On | 22 | 22.54 | -0.54 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 20.8 | Tue | School Day | On | On | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0.3315
| 16:00 | 20.5 | Tue | School Day | On | On | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0.41437
| 17:00 | 19.5 | Tue | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 18:00 | 18.7 | Tue | School Day | On | On | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0.91161
| 19:00 | 18.5 | Tue | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 20:00 | 18.8 | Tue | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 21:00 | 18.8 | Tue | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 22:00 | 19.3 | Tue | School Day | Off | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 23:00 | 18.3 | Tue | School Day | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
Wed, 25/May | 24:00 | 18 | Wed | School Day | Off | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 1:00 | 18.2 | Wed | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 2:00 | 17.6 | Wed | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 3:00 | 17.1 | Wed | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 4:00 | 16.4 | Wed | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 5:00 | 15.8 | Wed | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 6:00 | 15.4 | Wed | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 7:00 | 15.1 | Wed | School Day | On | On | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 1.9061
| 8:00 | 14.7 | Wed | School Day | On | On | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 2.0166
| 9:00 | 14.8 | Wed | School Day | On | On | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 1.989
| 10:00 | 14.6 | Wed | School Day | On | On | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 2.0442
| 11:00 | 14.9 | Wed | School Day | On | On | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 1.9614
| 12:00 | 15.6 | Wed | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 13:00 | 16.7 | Wed | School Day | On | On | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 1.4641
| 14:00 | 17.3 | Wed | School Day | On | On | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 1.2984
| 15:00 | 18.1 | Wed | School Day | On | On | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 1.0774
| 16:00 | 18.7 | Wed | School Day | On | On | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0.91161
| 17:00 | 18 | Wed | School Day | On | On | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 1.105
| 18:00 | 16 | Wed | School Day | On | On | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 1.6575
| 19:00 | 15.1 | Wed | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 20:00 | 14.4 | Wed | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 21:00 | 13.4 | Wed | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 22:00 | 13 | Wed | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 23:00 | 12.7 | Wed | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
Thu, 26/May | 24:00 | 12.3 | Thu | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 1:00 | 12.2 | Thu | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 2:00 | 12 | Thu | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 3:00 | 12 | Thu | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 4:00 | 12 | Thu | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 5:00 | 12 | Thu | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 6:00 | 11.7 | Thu | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 7:00 | 11.6 | Thu | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 8:00 | 11.5 | Thu | School Day | On | On | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 2.9006
| 9:00 | 12 | Thu | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 10:00 | 13.6 | Thu | School Day | On | On | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 2.3205
| 11:00 | 15.1 | Thu | School Day | On | On | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 1.9061
| 12:00 | 17.1 | Thu | School Day | On | On | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 1.3536
| 13:00 | 17.8 | Thu | School Day | On | On | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 1.1602
| 14:00 | 18.8 | Thu | School Day | On | On | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0.88399
| 15:00 | 19.9 | Thu | School Day | On | On | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0.58012
| 16:00 | 20 | Thu | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 17:00 | 19.9 | Thu | School Day | On | On | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0.58012
| 18:00 | 19.3 | Thu | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 19:00 | 18.9 | Thu | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 20:00 | 17.7 | Thu | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 21:00 | 16.1 | Thu | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 22:00 | 14.4 | Thu | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 23:00 | 12.7 | Thu | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
Fri, 27/May | 24:00 | 11.3 | Fri | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 1:00 | 10.3 | Fri | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 2:00 | 9.7 | Fri | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 3:00 | 9.2 | Fri | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 4:00 | 8.9 | Fri | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 5:00 | 8.4 | Fri | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 6:00 | 8.3 | Fri | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 7:00 | 8.4 | Fri | School Day | On | On | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 3.757
| 8:00 | 9.5 | Fri | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 9:00 | 11.2 | Fri | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 10:00 | 12.6 | Fri | School Day | On | On | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 2.5967
| 11:00 | 14.1 | Fri | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 12:00 | 15.5 | Fri | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 13:00 | 16.8 | Fri | School Day | On | On | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 1.4365
| 14:00 | 18.1 | Fri | School Day | On | On | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 1.0774
| 15:00 | 19.4 | Fri | School Day | On | On | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0.71824
| 16:00 | 19.5 | Fri | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 17:00 | 19.9 | Fri | School Day | On | On | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0.58012
| 18:00 | 19.5 | Fri | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 19:00 | 19.1 | Fri | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 20:00 | 18.6 | Fri | School Day | Off | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 21:00 | 17.8 | Fri | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 22:00 | 16.5 | Fri | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 23:00 | 15.1 | Fri | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
Sat, 28/May | 24:00 | 13.7 | Sat | WE | Off | OFF | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 1:00 | 12.6 | Sat | WE | Off | OFF | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 2:00 | 11.3 | Sat | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 3:00 | 10.8 | Sat | WE | Off | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 4:00 | 9.5 | Sat | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 5:00 | 8.8 | Sat | WE | Off | OFF | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 6:00 | 8.1 | Sat | WE | Off | OFF | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 7:00 | 8.3 | Sat | WE | On | OFF | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 8:00 | 9.8 | Sat | WE | On | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 9:00 | 12.1 | Sat | WE | On | OFF | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 10:00 | 13.8 | Sat | WE | On | OFF | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 11:00 | 15.2 | Sat | WE | On | OFF | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 12:00 | 16.5 | Sat | WE | On | OFF | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 13:00 | 18.1 | Sat | WE | On | OFF | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 14:00 | 19 | Sat | WE | On | OFF | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 15:00 | 20.7 | Sat | WE | On | OFF | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 16:00 | 20.9 | Sat | WE | On | OFF | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 17:00 | 21.8 | Sat | WE | On | OFF | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0
| 18:00 | 21.9 | Sat | WE | On | OFF | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 19:00 | 21.7 | Sat | WE | Off | OFF | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 20:00 | 21.2 | Sat | WE | Off | OFF | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 21:00 | 20.7 | Sat | WE | Off | OFF | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 22:00 | 19.6 | Sat | WE | Off | OFF | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 23:00 | 18.8 | Sat | WE | Off | OFF | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
Sun, 29/May | 24:00 | 17.8 | Sun | WE | Off | OFF | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 1:00 | 15.6 | Sun | WE | Off | OFF | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 2:00 | 15.8 | Sun | WE | Off | OFF | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 3:00 | 15.1 | Sun | WE | Off | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 4:00 | 14.5 | Sun | WE | Off | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 5:00 | 13.1 | Sun | WE | Off | OFF | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 6:00 | 11.9 | Sun | WE | Off | OFF | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 7:00 | 11.9 | Sun | WE | On | OFF | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 8:00 | 12.2 | Sun | WE | On | OFF | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 9:00 | 14 | Sun | WE | On | OFF | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 10:00 | 16.1 | Sun | WE | On | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 11:00 | 18 | Sun | WE | On | OFF | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 12:00 | 19.6 | Sun | WE | On | OFF | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 13:00 | 21 | Sun | WE | On | OFF | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 14:00 | 21.9 | Sun | WE | On | OFF | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 15:00 | 22 | Sun | WE | On | OFF | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23.2 | Sun | WE | On | OFF | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 22.7 | Sun | WE | On | OFF | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.8 | Sun | WE | On | OFF | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.3 | Sun | WE | Off | OFF | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 21.6 | Sun | WE | Off | OFF | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 21:00 | 20.6 | Sun | WE | Off | OFF | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 22:00 | 18.9 | Sun | WE | Off | OFF | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 23:00 | 17.6 | Sun | WE | Off | OFF | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
Mon, 30/May | 24:00 | 17 | Mon | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 1:00 | 16.3 | Mon | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 2:00 | 13.7 | Mon | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 3:00 | 12.8 | Mon | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 4:00 | 12.1 | Mon | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 5:00 | 12.2 | Mon | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 6:00 | 11.8 | Mon | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 7:00 | 11.5 | Mon | School Day | On | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 8:00 | 11.6 | Mon | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 9:00 | 12.7 | Mon | School Day | On | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 10:00 | 12.4 | Mon | School Day | On | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 11:00 | 12 | Mon | School Day | On | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 12:00 | 13 | Mon | School Day | On | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 13:00 | 15 | Mon | School Day | On | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 14:00 | 14.4 | Mon | School Day | On | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 15:00 | 16.2 | Mon | School Day | On | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 16:00 | 16.4 | Mon | School Day | On | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 17:00 | 15.8 | Mon | School Day | On | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 18:00 | 15.1 | Mon | School Day | On | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 19:00 | 15.3 | Mon | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 20:00 | 15.3 | Mon | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 21:00 | 14.2 | Mon | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 22:00 | 12.6 | Mon | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 23:00 | 11.5 | Mon | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
Tue, 31/May | 24:00 | 10.5 | Tue | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 1:00 | 9.7 | Tue | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 2:00 | 9.2 | Tue | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 3:00 | 8.2 | Tue | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 4:00 | 7.9 | Tue | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 5:00 | 6.1 | Tue | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 6:00 | 5.3 | Tue | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 7:00 | 5.9 | Tue | School Day | On | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 8:00 | 7.1 | Tue | School Day | On | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 9:00 | 9.9 | Tue | School Day | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 10:00 | 11.6 | Tue | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 11:00 | 13.1 | Tue | School Day | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 12:00 | 14.5 | Tue | School Day | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 13:00 | 14.5 | Tue | School Day | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 14:00 | 14.9 | Tue | School Day | On | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 15:00 | 15.5 | Tue | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 16:00 | 16 | Tue | School Day | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 17:00 | 15.5 | Tue | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 18:00 | 16 | Tue | School Day | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 19:00 | 15.2 | Tue | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 20:00 | 15.1 | Tue | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 21:00 | 14.2 | Tue | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 22:00 | 13.6 | Tue | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 23:00 | 13 | Tue | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
Wed, 01/Jun | 24:00 | 12.4 | Wed | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 1:00 | 11.2 | Wed | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 2:00 | 10.7 | Wed | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 3:00 | 10.3 | Wed | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 4:00 | 10 | Wed | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 5:00 | 9.4 | Wed | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 6:00 | 9.4 | Wed | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 7:00 | 9.5 | Wed | School Day | On | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 8:00 | 9.9 | Wed | School Day | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 9:00 | 10.7 | Wed | School Day | On | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 10:00 | 11.3 | Wed | School Day | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 11:00 | 12.3 | Wed | School Day | On | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 12:00 | 12.1 | Wed | School Day | On | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 13:00 | 13.5 | Wed | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 14:00 | 13.9 | Wed | School Day | On | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 15:00 | 13.7 | Wed | School Day | On | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 16:00 | 13.5 | Wed | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 17:00 | 14 | Wed | School Day | On | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 18:00 | 13 | Wed | School Day | On | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 19:00 | 12.7 | Wed | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 20:00 | 11 | Wed | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 21:00 | 10.7 | Wed | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 22:00 | 10.4 | Wed | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 23:00 | 10.3 | Wed | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
Thu, 02/Jun | 24:00 | 10.1 | Thu | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 1:00 | 10.1 | Thu | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 2:00 | 9.7 | Thu | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 3:00 | 9.7 | Thu | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 4:00 | 8.7 | Thu | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 5:00 | 7.7 | Thu | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 6:00 | 6.4 | Thu | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 7:00 | 6.7 | Thu | School Day | On | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 8:00 | 8.3 | Thu | School Day | On | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 9:00 | 10.1 | Thu | School Day | On | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 10:00 | 11.9 | Thu | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 11:00 | 12.3 | Thu | School Day | On | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 12:00 | 13.1 | Thu | School Day | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 13:00 | 14.3 | Thu | School Day | On | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 14:00 | 14.8 | Thu | School Day | On | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 15:00 | 16 | Thu | School Day | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 16:00 | 16 | Thu | School Day | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 17:00 | 15.9 | Thu | School Day | On | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 18:00 | 15.6 | Thu | School Day | On | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 19:00 | 16 | Thu | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 20:00 | 15.4 | Thu | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 21:00 | 14.6 | Thu | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 22:00 | 13.8 | Thu | School Day | Off | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 23:00 | 13 | Thu | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
Fri, 03/Jun | 24:00 | 11.1 | Fri | School Day | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 1:00 | 10.3 | Fri | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 2:00 | 9.4 | Fri | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 3:00 | 8.5 | Fri | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 4:00 | 7.4 | Fri | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 5:00 | 7.1 | Fri | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 6:00 | 6.8 | Fri | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 7:00 | 6.9 | Fri | School Day | On | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 8:00 | 8.6 | Fri | School Day | On | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 9:00 | 10.9 | Fri | School Day | On | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 10:00 | 12.1 | Fri | School Day | On | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 11:00 | 13 | Fri | School Day | On | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 12:00 | 14.1 | Fri | School Day | On | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 13:00 | 15.8 | Fri | School Day | On | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 14:00 | 14.6 | Fri | School Day | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 15:00 | 14.6 | Fri | School Day | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 16:00 | 14.4 | Fri | School Day | On | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 17:00 | 14.2 | Fri | School Day | On | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 18:00 | 14.2 | Fri | School Day | On | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 19:00 | 14.5 | Fri | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 20:00 | 14.1 | Fri | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 21:00 | 13.7 | Fri | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 22:00 | 12.4 | Fri | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 23:00 | 11.3 | Fri | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
Sat, 04/Jun | 24:00 | 10.9 | Sat | WE | Off | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 1:00 | 9.5 | Sat | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 2:00 | 9.2 | Sat | WE | Off | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 3:00 | 8.2 | Sat | WE | Off | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 4:00 | 7.6 | Sat | WE | Off | OFF | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 5:00 | 6.9 | Sat | WE | Off | OFF | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 6:00 | 6.6 | Sat | WE | Off | OFF | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 7:00 | 7.1 | Sat | WE | On | OFF | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 8:00 | 8.2 | Sat | WE | On | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 9:00 | 10.3 | Sat | WE | On | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 10:00 | 11 | Sat | WE | On | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 11:00 | 12.2 | Sat | WE | On | OFF | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 12:00 | 13 | Sat | WE | On | OFF | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 13:00 | 13 | Sat | WE | On | OFF | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 14:00 | 14.5 | Sat | WE | On | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 15:00 | 15.4 | Sat | WE | On | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 16:00 | 16 | Sat | WE | On | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 17:00 | 16.6 | Sat | WE | On | OFF | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 18:00 | 17 | Sat | WE | On | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 19:00 | 15.9 | Sat | WE | Off | OFF | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 20:00 | 15.8 | Sat | WE | Off | OFF | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 21:00 | 14.5 | Sat | WE | Off | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 22:00 | 14.1 | Sat | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 23:00 | 12.5 | Sat | WE | Off | OFF | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
Sun, 05/Jun | 24:00 | 11.3 | Sun | WE | Off | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 1:00 | 10.4 | Sun | WE | Off | OFF | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 2:00 | 9.1 | Sun | WE | Off | OFF | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 3:00 | 7.4 | Sun | WE | Off | OFF | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 4:00 | 6.5 | Sun | WE | Off | OFF | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 5:00 | 6.1 | Sun | WE | Off | OFF | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 6:00 | 6.3 | Sun | WE | Off | OFF | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 7:00 | 6.5 | Sun | WE | On | OFF | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 8:00 | 8.5 | Sun | WE | On | OFF | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 9:00 | 10.5 | Sun | WE | On | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 10:00 | 12.5 | Sun | WE | On | OFF | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 11:00 | 14.9 | Sun | WE | On | OFF | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 12:00 | 15.6 | Sun | WE | On | OFF | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 13:00 | 15.9 | Sun | WE | On | OFF | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 14:00 | 17.4 | Sun | WE | On | OFF | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 15:00 | 18 | Sun | WE | On | OFF | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 16:00 | 17.1 | Sun | WE | On | OFF | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 17:00 | 17.5 | Sun | WE | On | OFF | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 18:00 | 18 | Sun | WE | On | OFF | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 19:00 | 17.3 | Sun | WE | Off | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 20:00 | 16.5 | Sun | WE | Off | OFF | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 21:00 | 11.8 | Sun | WE | Off | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 22:00 | 12.1 | Sun | WE | Off | OFF | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 23:00 | 11.5 | Sun | WE | Off | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
Mon, 06/Jun | 24:00 | 11.4 | Mon | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 1:00 | 11 | Mon | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 2:00 | 11 | Mon | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 3:00 | 10.7 | Mon | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 4:00 | 10.6 | Mon | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 5:00 | 10.4 | Mon | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 6:00 | 10.4 | Mon | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 7:00 | 10.3 | Mon | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 8:00 | 10.5 | Mon | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 9:00 | 10.6 | Mon | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 10:00 | 10.9 | Mon | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 11:00 | 12.1 | Mon | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 12:00 | 12.8 | Mon | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 13:00 | 12.4 | Mon | School Day | On | On | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 2.652
| 14:00 | 12.3 | Mon | School Day | On | On | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 2.6796
| 15:00 | 12.6 | Mon | School Day | On | On | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 2.5967
| 16:00 | 12.8 | Mon | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 17:00 | 12.2 | Mon | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 18:00 | 12.2 | Mon | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 19:00 | 12.9 | Mon | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 20:00 | 13 | Mon | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 21:00 | 10.8 | Mon | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 22:00 | 10.8 | Mon | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 23:00 | 11 | Mon | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
Tue, 07/Jun | 24:00 | 10.9 | Tue | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 1:00 | 10.8 | Tue | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 2:00 | 10.9 | Tue | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 3:00 | 10.7 | Tue | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 4:00 | 10.8 | Tue | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 5:00 | 10.9 | Tue | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 6:00 | 10.9 | Tue | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 7:00 | 11.4 | Tue | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 8:00 | 11.7 | Tue | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 9:00 | 11.7 | Tue | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 10:00 | 12.2 | Tue | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 11:00 | 12.4 | Tue | School Day | On | On | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 2.652
| 12:00 | 12.7 | Tue | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 13:00 | 14.9 | Tue | School Day | On | On | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 1.9614
| 14:00 | 15.7 | Tue | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 15:00 | 16.3 | Tue | School Day | On | On | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 1.5746
| 16:00 | 15.2 | Tue | School Day | On | On | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 1.8785
| 17:00 | 15.6 | Tue | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 18:00 | 17.2 | Tue | School Day | On | On | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 1.326
| 19:00 | 16.6 | Tue | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 20:00 | 16 | Tue | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 21:00 | 15.9 | Tue | School Day | Off | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 22:00 | 14.7 | Tue | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 23:00 | 13.9 | Tue | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
Wed, 08/Jun | 24:00 | 12.8 | Wed | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 1:00 | 11.9 | Wed | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 2:00 | 10.9 | Wed | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 3:00 | 10 | Wed | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 4:00 | 9 | Wed | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 5:00 | 8.9 | Wed | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 6:00 | 9.1 | Wed | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 7:00 | 9.4 | Wed | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 8:00 | 9.9 | Wed | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 9:00 | 11.5 | Wed | School Day | On | On | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 2.9006
| 10:00 | 13.1 | Wed | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 11:00 | 14 | Wed | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 12:00 | 15.6 | Wed | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 13:00 | 16.1 | Wed | School Day | On | On | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 1.6299
| 14:00 | 17 | Wed | School Day | On | On | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 1.3812
| 15:00 | 16.2 | Wed | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 16:00 | 14.4 | Wed | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 17:00 | 13.2 | Wed | School Day | On | On | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 2.431
| 18:00 | 12.9 | Wed | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 19:00 | 12.8 | Wed | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 20:00 | 13 | Wed | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 21:00 | 12.6 | Wed | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 22:00 | 12 | Wed | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 23:00 | 11.7 | Wed | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
Thu, 09/Jun | 24:00 | 11.9 | Thu | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 1:00 | 11.7 | Thu | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 2:00 | 11.7 | Thu | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 3:00 | 11.5 | Thu | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 4:00 | 11.2 | Thu | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 5:00 | 10.9 | Thu | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 6:00 | 10 | Thu | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 7:00 | 10.2 | Thu | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 8:00 | 11.9 | Thu | School Day | On | On | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 2.7901
| 9:00 | 12.7 | Thu | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 10:00 | 13.5 | Thu | School Day | On | On | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 2.3481
| 11:00 | 15 | Thu | School Day | On | On | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 1.9337
| 12:00 | 15.4 | Thu | School Day | On | On | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 1.8232
| 13:00 | 15.3 | Thu | School Day | On | On | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 1.8509
| 14:00 | 16.9 | Thu | School Day | On | On | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 1.4089
| 15:00 | 19.3 | Thu | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 16:00 | 20.1 | Thu | School Day | On | On | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0.52487
| 17:00 | 19.5 | Thu | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 18:00 | 19.5 | Thu | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 19:00 | 19 | Thu | School Day | Off | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 20:00 | 19.1 | Thu | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 21:00 | 18.1 | Thu | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 22:00 | 17.1 | Thu | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 23:00 | 16.8 | Thu | School Day | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
Fri, 10/Jun | 24:00 | 16.7 | Fri | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 1:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 2:00 | 14.8 | Fri | School Day | Off | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 3:00 | 14.2 | Fri | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 4:00 | 14.6 | Fri | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 5:00 | 13.6 | Fri | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 6:00 | 13.7 | Fri | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 7:00 | 13.4 | Fri | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 8:00 | 13.3 | Fri | School Day | On | On | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 2.4033
| 9:00 | 14.1 | Fri | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 10:00 | 15.9 | Fri | School Day | On | On | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 1.6851
| 11:00 | 18.1 | Fri | School Day | On | On | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 1.0774
| 12:00 | 19.5 | Fri | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 13:00 | 21.4 | Fri | School Day | On | On | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0.16575
| 14:00 | 22 | Fri | School Day | On | On | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 21.7 | Fri | School Day | On | On | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0.082874
| 16:00 | 22 | Fri | School Day | On | On | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 21.8 | Fri | School Day | On | On | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0.055249
| 18:00 | 20.5 | Fri | School Day | On | On | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0.41437
| 19:00 | 19.9 | Fri | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 20:00 | 20 | Fri | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 21:00 | 19.5 | Fri | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 22:00 | 18.5 | Fri | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 23:00 | 17.3 | Fri | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
Sat, 11/Jun | 24:00 | 16.3 | Sat | WE | Off | OFF | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 1:00 | 15.2 | Sat | WE | Off | OFF | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 2:00 | 14.3 | Sat | WE | Off | OFF | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 3:00 | 13.7 | Sat | WE | Off | OFF | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 4:00 | 13.2 | Sat | WE | Off | OFF | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 5:00 | 13.2 | Sat | WE | Off | OFF | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 6:00 | 12.3 | Sat | WE | Off | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 7:00 | 12.2 | Sat | WE | On | OFF | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 8:00 | 12.7 | Sat | WE | On | OFF | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 9:00 | 13.3 | Sat | WE | On | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 10:00 | 14.8 | Sat | WE | On | OFF | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 11:00 | 18.3 | Sat | WE | On | OFF | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 12:00 | 20.3 | Sat | WE | On | OFF | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 13:00 | 22 | Sat | WE | On | OFF | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 23.1 | Sat | WE | On | OFF | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23 | Sat | WE | On | OFF | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23.4 | Sat | WE | On | OFF | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23.7 | Sat | WE | On | OFF | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 23.9 | Sat | WE | On | OFF | 22 | 22.19 | -0.19 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.4 | Sat | WE | Off | OFF | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 21.5 | Sat | WE | Off | OFF | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 21:00 | 21.6 | Sat | WE | Off | OFF | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 22:00 | 20.4 | Sat | WE | Off | OFF | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 23:00 | 20 | Sat | WE | Off | OFF | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
Sun, 12/Jun | 24:00 | 18.9 | Sun | WE | Off | OFF | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 1:00 | 17.9 | Sun | WE | Off | OFF | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 2:00 | 17.3 | Sun | WE | Off | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 3:00 | 16.7 | Sun | WE | Off | OFF | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 4:00 | 16.6 | Sun | WE | Off | OFF | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 5:00 | 16 | Sun | WE | Off | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 6:00 | 16.6 | Sun | WE | Off | OFF | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 7:00 | 17 | Sun | WE | On | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 8:00 | 17.7 | Sun | WE | On | OFF | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 9:00 | 19 | Sun | WE | On | OFF | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 10:00 | 20.7 | Sun | WE | On | OFF | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 11:00 | 22.7 | Sun | WE | On | OFF | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25.2 | Sun | WE | On | OFF | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 26.4 | Sun | WE | On | OFF | 22 | 22.44 | -0.44 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 26.6 | Sun | WE | On | OFF | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26.3 | Sun | WE | On | OFF | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 28.6 | Sun | WE | On | OFF | 22 | 22.66 | -0.66 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 28.8 | Sun | WE | On | OFF | 22 | 22.68 | -0.68 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 28.6 | Sun | WE | On | OFF | 22 | 22.66 | -0.66 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 28.3 | Sun | WE | Off | OFF | 22 | 22.63 | -0.63 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 27.5 | Sun | WE | Off | OFF | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 26.4 | Sun | WE | Off | OFF | 22 | 22.44 | -0.44 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 25 | Sun | WE | Off | OFF | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 23.3 | Sun | WE | Off | OFF | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Mon, 13/Jun | 24:00 | 22.1 | Mon | School Day | Off | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 20 | Mon | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 2:00 | 18.9 | Mon | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 3:00 | 18.3 | Mon | School Day | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 4:00 | 18 | Mon | School Day | Off | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 5:00 | 17.4 | Mon | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 6:00 | 16.5 | Mon | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 7:00 | 17.1 | Mon | School Day | On | On | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 1.3536
| 8:00 | 19.3 | Mon | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 9:00 | 20 | Mon | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 10:00 | 22 | Mon | School Day | On | On | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 11:00 | 24.5 | Mon | School Day | On | On | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25.4 | Mon | School Day | On | On | 22 | 22.34 | -0.34 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 26.3 | Mon | School Day | On | On | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 27.3 | Mon | School Day | On | On | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27.7 | Mon | School Day | On | On | 22 | 22.57 | -0.57 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 28.8 | Mon | School Day | On | On | 22 | 22.68 | -0.68 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 28.7 | Mon | School Day | On | On | 22 | 22.67 | -0.67 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 28 | Mon | School Day | On | On | 22 | 22.6 | -0.6 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 27.7 | Mon | School Day | Off | Off | 22 | 22.57 | -0.57 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 26.7 | Mon | School Day | Off | Off | 22 | 22.47 | -0.47 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 26.2 | Mon | School Day | Off | Off | 22 | 22.42 | -0.42 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 24.9 | Mon | School Day | Off | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 22.3 | Mon | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Tue, 14/Jun | 24:00 | 20.8 | Tue | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 1:00 | 20.8 | Tue | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 2:00 | 20.8 | Tue | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 3:00 | 19.4 | Tue | School Day | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 4:00 | 17.9 | Tue | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 5:00 | 17 | Tue | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 6:00 | 16.3 | Tue | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 7:00 | 16.2 | Tue | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 8:00 | 17.6 | Tue | School Day | On | On | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 1.2155
| 9:00 | 20 | Tue | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 10:00 | 21.6 | Tue | School Day | On | On | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0.1105
| 11:00 | 23.1 | Tue | School Day | On | On | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25.6 | Tue | School Day | On | On | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 27.5 | Tue | School Day | On | On | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 28.1 | Tue | School Day | On | On | 22 | 22.61 | -0.61 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27.5 | Tue | School Day | On | On | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26.7 | Tue | School Day | On | On | 22 | 22.47 | -0.47 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.3 | Tue | School Day | On | On | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.6 | Tue | School Day | On | On | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25 | Tue | School Day | Off | Off | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25.1 | Tue | School Day | Off | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24.8 | Tue | School Day | Off | Off | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23.8 | Tue | School Day | Off | Off | 22 | 22.18 | -0.18 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 23.2 | Tue | School Day | Off | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Wed, 15/Jun | 24:00 | 22.4 | Wed | School Day | Off | Off | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 21.9 | Wed | School Day | Off | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 2:00 | 21.1 | Wed | School Day | Off | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 3:00 | 20 | Wed | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 4:00 | 18.9 | Wed | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 5:00 | 18.2 | Wed | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 6:00 | 17 | Wed | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 7:00 | 16.6 | Wed | School Day | On | On | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 1.4917
| 8:00 | 17.3 | Wed | School Day | On | On | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 1.2984
| 9:00 | 17.9 | Wed | School Day | On | On | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 1.1326
| 10:00 | 19.2 | Wed | School Day | On | On | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0.77349
| 11:00 | 20.8 | Wed | School Day | On | On | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0.3315
| 12:00 | 23.5 | Wed | School Day | On | On | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 24.9 | Wed | School Day | On | On | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 26 | Wed | School Day | On | On | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27.3 | Wed | School Day | On | On | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27 | Wed | School Day | On | On | 22 | 22.5 | -0.5 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 28 | Wed | School Day | On | On | 22 | 22.6 | -0.6 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 28.6 | Wed | School Day | On | On | 22 | 22.66 | -0.66 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 27.5 | Wed | School Day | Off | Off | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 26.9 | Wed | School Day | Off | Off | 22 | 22.49 | -0.49 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24.3 | Wed | School Day | Off | Off | 22 | 22.23 | -0.23 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.3 | Wed | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 20.9 | Wed | School Day | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
Thu, 16/Jun | 24:00 | 19.7 | Thu | School Day | Off | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 1:00 | 18.7 | Thu | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 2:00 | 17.2 | Thu | School Day | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 3:00 | 16.5 | Thu | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 4:00 | 16.3 | Thu | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 5:00 | 15.9 | Thu | School Day | Off | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 6:00 | 15.9 | Thu | School Day | Off | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 7:00 | 15.9 | Thu | School Day | On | On | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 1.6851
| 8:00 | 17 | Thu | School Day | On | On | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 1.3812
| 9:00 | 18.9 | Thu | School Day | On | On | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0.85637
| 10:00 | 20.8 | Thu | School Day | On | On | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0.3315
| 11:00 | 22.9 | Thu | School Day | On | On | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 24.3 | Thu | School Day | On | On | 22 | 22.23 | -0.23 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 25.3 | Thu | School Day | On | On | 22 | 22.33 | -0.33 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 26.5 | Thu | School Day | On | On | 22 | 22.45 | -0.45 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27 | Thu | School Day | On | On | 22 | 22.5 | -0.5 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26.3 | Thu | School Day | On | On | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26.8 | Thu | School Day | On | On | 22 | 22.48 | -0.48 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 27.4 | Thu | School Day | On | On | 22 | 22.54 | -0.54 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 26.7 | Thu | School Day | Off | Off | 22 | 22.47 | -0.47 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 26.1 | Thu | School Day | Off | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24.2 | Thu | School Day | Off | Off | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.6 | Thu | School Day | Off | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 20.1 | Thu | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
Fri, 17/Jun | 24:00 | 19.8 | Fri | School Day | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 1:00 | 17.7 | Fri | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 2:00 | 17.5 | Fri | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 3:00 | 16.9 | Fri | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 4:00 | 16.8 | Fri | School Day | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 5:00 | 16.3 | Fri | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 6:00 | 15.7 | Fri | School Day | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 7:00 | 16.3 | Fri | School Day | On | On | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 1.5746
| 8:00 | 16.9 | Fri | School Day | On | On | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 1.4089
| 9:00 | 18.5 | Fri | School Day | On | On | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0.96686
| 10:00 | 20.9 | Fri | School Day | On | On | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0.30387
| 11:00 | 23 | Fri | School Day | On | On | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25 | Fri | School Day | On | On | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 25.8 | Fri | School Day | On | On | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 26.5 | Fri | School Day | On | On | 22 | 22.45 | -0.45 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27.3 | Fri | School Day | On | On | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27.9 | Fri | School Day | On | On | 22 | 22.59 | -0.59 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.9 | Fri | School Day | On | On | 22 | 22.59 | -0.59 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 28.1 | Fri | School Day | On | On | 22 | 22.61 | -0.61 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 27.5 | Fri | School Day | Off | Off | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25.2 | Fri | School Day | Off | Off | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23 | Fri | School Day | Off | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 21.5 | Fri | School Day | Off | Off | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 23:00 | 19.8 | Fri | School Day | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
Sat, 18/Jun | 24:00 | 19.5 | Sat | WE | Off | OFF | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 1:00 | 17.7 | Sat | WE | Off | OFF | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 2:00 | 17.1 | Sat | WE | Off | OFF | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 3:00 | 16.1 | Sat | WE | Off | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 4:00 | 15.4 | Sat | WE | Off | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 5:00 | 14.8 | Sat | WE | Off | OFF | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 6:00 | 13.9 | Sat | WE | Off | OFF | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 7:00 | 14 | Sat | WE | On | OFF | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 8:00 | 14.9 | Sat | WE | On | OFF | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 9:00 | 17.4 | Sat | WE | On | OFF | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 10:00 | 19.1 | Sat | WE | On | OFF | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 11:00 | 21.2 | Sat | WE | On | OFF | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 12:00 | 23.9 | Sat | WE | On | OFF | 22 | 22.19 | -0.19 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 24.8 | Sat | WE | On | OFF | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 25.9 | Sat | WE | On | OFF | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26.4 | Sat | WE | On | OFF | 22 | 22.44 | -0.44 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27.2 | Sat | WE | On | OFF | 22 | 22.52 | -0.52 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.1 | Sat | WE | On | OFF | 22 | 22.51 | -0.51 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 27.4 | Sat | WE | On | OFF | 22 | 22.54 | -0.54 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 27.1 | Sat | WE | Off | OFF | 22 | 22.51 | -0.51 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 26.5 | Sat | WE | Off | OFF | 22 | 22.45 | -0.45 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 25.3 | Sat | WE | Off | OFF | 22 | 22.33 | -0.33 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23.3 | Sat | WE | Off | OFF | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.7 | Sat | WE | Off | OFF | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
Sun, 19/Jun | 24:00 | 19.8 | Sun | WE | Off | OFF | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 1:00 | 18.4 | Sun | WE | Off | OFF | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 2:00 | 17.3 | Sun | WE | Off | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 3:00 | 15.9 | Sun | WE | Off | OFF | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 4:00 | 15 | Sun | WE | Off | OFF | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 5:00 | 14.5 | Sun | WE | Off | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 6:00 | 14.5 | Sun | WE | Off | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 7:00 | 14.8 | Sun | WE | On | OFF | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 8:00 | 16 | Sun | WE | On | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 9:00 | 16.9 | Sun | WE | On | OFF | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 10:00 | 18.8 | Sun | WE | On | OFF | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 11:00 | 20.6 | Sun | WE | On | OFF | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 12:00 | 23.5 | Sun | WE | On | OFF | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 25.6 | Sun | WE | On | OFF | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 26.6 | Sun | WE | On | OFF | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27.9 | Sun | WE | On | OFF | 22 | 22.59 | -0.59 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 28.6 | Sun | WE | On | OFF | 22 | 22.66 | -0.66 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 30 | Sun | WE | On | OFF | 22 | 22.8 | -0.8 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 29.7 | Sun | WE | On | OFF | 22 | 22.77 | -0.77 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 28.6 | Sun | WE | Off | OFF | 22 | 22.66 | -0.66 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 28 | Sun | WE | Off | OFF | 22 | 22.6 | -0.6 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 26.6 | Sun | WE | Off | OFF | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 24.3 | Sun | WE | Off | OFF | 22 | 22.23 | -0.23 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 22.2 | Sun | WE | Off | OFF | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Mon, 20/Jun | 24:00 | 20.9 | Mon | School Day | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 1:00 | 20.6 | Mon | School Day | Off | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 2:00 | 20.2 | Mon | School Day | Off | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 3:00 | 18.8 | Mon | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 4:00 | 17.5 | Mon | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 5:00 | 16.5 | Mon | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 6:00 | 16 | Mon | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 7:00 | 15.9 | Mon | School Day | On | On | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 1.6851
| 8:00 | 18 | Mon | School Day | On | On | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 1.105
| 9:00 | 19.7 | Mon | School Day | On | On | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0.63537
| 10:00 | 21.8 | Mon | School Day | On | On | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0.055249
| 11:00 | 23.6 | Mon | School Day | On | On | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25.6 | Mon | School Day | On | On | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 27.7 | Mon | School Day | On | On | 22 | 22.57 | -0.57 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 28.7 | Mon | School Day | On | On | 22 | 22.67 | -0.67 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 29.4 | Mon | School Day | On | On | 22 | 22.74 | -0.74 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 30 | Mon | School Day | On | On | 22 | 22.8 | -0.8 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 30.7 | Mon | School Day | On | On | 22 | 22.87 | -0.87 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 30.3 | Mon | School Day | On | On | 22 | 22.83 | -0.83 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 30.9 | Mon | School Day | Off | Off | 22 | 22.89 | -0.89 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 30 | Mon | School Day | Off | Off | 22 | 22.8 | -0.8 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 29 | Mon | School Day | Off | Off | 22 | 22.7 | -0.7 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 28 | Mon | School Day | Off | Off | 22 | 22.6 | -0.6 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 26.8 | Mon | School Day | Off | Off | 22 | 22.48 | -0.48 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Tue, 21/Jun | 24:00 | 25.5 | Tue | School Day | Off | Off | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 22.8 | Tue | School Day | Off | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 2:00 | 22.3 | Tue | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 3:00 | 21 | Tue | School Day | Off | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 4:00 | 19.9 | Tue | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 5:00 | 17.7 | Tue | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 6:00 | 17 | Tue | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 7:00 | 16.1 | Tue | School Day | On | On | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 1.6299
| 8:00 | 15.7 | Tue | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 9:00 | 15.8 | Tue | School Day | On | On | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 1.7127
| 10:00 | 17.4 | Tue | School Day | On | On | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 1.2707
| 11:00 | 19.1 | Tue | School Day | On | On | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0.80112
| 12:00 | 21.2 | Tue | School Day | On | On | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0.221
| 13:00 | 22.5 | Tue | School Day | On | On | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 22.6 | Tue | School Day | On | On | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.3 | Tue | School Day | On | On | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23.5 | Tue | School Day | On | On | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 22.8 | Tue | School Day | On | On | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.8 | Tue | School Day | On | On | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22 | Tue | School Day | Off | Off | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 21.3 | Tue | School Day | Off | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 21:00 | 21.2 | Tue | School Day | Off | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 22:00 | 20.3 | Tue | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 23:00 | 19.3 | Tue | School Day | Off | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
Wed, 22/Jun | 24:00 | 17.1 | Wed | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 1:00 | 16.1 | Wed | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 2:00 | 15.8 | Wed | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 3:00 | 15.2 | Wed | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 4:00 | 15.1 | Wed | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 5:00 | 14.8 | Wed | School Day | Off | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 6:00 | 14.5 | Wed | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 7:00 | 14.5 | Wed | School Day | On | On | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 2.0719
| 8:00 | 14.4 | Wed | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 9:00 | 14.4 | Wed | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 10:00 | 15.1 | Wed | School Day | On | On | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 1.9061
| 11:00 | 15.4 | Wed | School Day | On | On | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 1.8232
| 12:00 | 15.6 | Wed | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 13:00 | 16.2 | Wed | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 14:00 | 17.4 | Wed | School Day | On | On | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 1.2707
| 15:00 | 18 | Wed | School Day | On | On | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 1.105
| 16:00 | 18.8 | Wed | School Day | On | On | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0.88399
| 17:00 | 19.9 | Wed | School Day | On | On | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0.58012
| 18:00 | 20.1 | Wed | School Day | On | On | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0.52487
| 19:00 | 20.2 | Wed | School Day | Off | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 20:00 | 20.4 | Wed | School Day | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 21:00 | 20.1 | Wed | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 22:00 | 19.5 | Wed | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 23:00 | 17.9 | Wed | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
Thu, 23/Jun | 24:00 | 17.5 | Thu | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 1:00 | 17 | Thu | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 2:00 | 16.4 | Thu | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 3:00 | 15.4 | Thu | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 4:00 | 14.6 | Thu | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 5:00 | 14.2 | Thu | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 6:00 | 13.2 | Thu | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 7:00 | 13.4 | Thu | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 8:00 | 14.6 | Thu | School Day | On | On | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 2.0442
| 9:00 | 15.9 | Thu | School Day | On | On | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 1.6851
| 10:00 | 16.9 | Thu | School Day | On | On | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 1.4089
| 11:00 | 18.6 | Thu | School Day | On | On | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0.93924
| 12:00 | 20.2 | Thu | School Day | On | On | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0.49724
| 13:00 | 21.7 | Thu | School Day | On | On | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0.082874
| 14:00 | 23.5 | Thu | School Day | On | On | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 24.4 | Thu | School Day | On | On | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 24.9 | Thu | School Day | On | On | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.3 | Thu | School Day | On | On | 22 | 22.33 | -0.33 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.6 | Thu | School Day | On | On | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.7 | Thu | School Day | Off | Off | 22 | 22.37 | -0.37 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25.2 | Thu | School Day | Off | Off | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24.2 | Thu | School Day | Off | Off | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23.1 | Thu | School Day | Off | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.6 | Thu | School Day | Off | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
Fri, 24/Jun | 24:00 | 20.4 | Fri | School Day | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 1:00 | 19.5 | Fri | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 2:00 | 16.4 | Fri | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 3:00 | 16.4 | Fri | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 4:00 | 15.3 | Fri | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 5:00 | 14.6 | Fri | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 6:00 | 14.1 | Fri | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 7:00 | 14.1 | Fri | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 8:00 | 15.2 | Fri | School Day | On | On | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 1.8785
| 9:00 | 16.6 | Fri | School Day | On | On | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 1.4917
| 10:00 | 17.8 | Fri | School Day | On | On | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 1.1602
| 11:00 | 19 | Fri | School Day | On | On | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0.82874
| 12:00 | 20.9 | Fri | School Day | On | On | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0.30387
| 13:00 | 21.9 | Fri | School Day | On | On | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0.027625
| 14:00 | 22.9 | Fri | School Day | On | On | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.5 | Fri | School Day | On | On | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 24.8 | Fri | School Day | On | On | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 24.4 | Fri | School Day | On | On | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 24.7 | Fri | School Day | On | On | 22 | 22.27 | -0.27 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.3 | Fri | School Day | Off | Off | 22 | 22.33 | -0.33 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.9 | Fri | School Day | Off | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24 | Fri | School Day | Off | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23.4 | Fri | School Day | Off | Off | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.6 | Fri | School Day | Off | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
Sat, 25/Jun | 24:00 | 20.4 | Sat | WE | Off | OFF | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 1:00 | 18.8 | Sat | WE | Off | OFF | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 2:00 | 17.1 | Sat | WE | Off | OFF | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 3:00 | 15 | Sat | WE | Off | OFF | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 4:00 | 14.5 | Sat | WE | Off | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 5:00 | 13.9 | Sat | WE | Off | OFF | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 6:00 | 13.4 | Sat | WE | Off | OFF | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 7:00 | 13.7 | Sat | WE | On | OFF | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 8:00 | 14.7 | Sat | WE | On | OFF | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 9:00 | 16.5 | Sat | WE | On | OFF | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 10:00 | 18.5 | Sat | WE | On | OFF | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 11:00 | 21.2 | Sat | WE | On | OFF | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 12:00 | 22.3 | Sat | WE | On | OFF | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 24.5 | Sat | WE | On | OFF | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 25.7 | Sat | WE | On | OFF | 22 | 22.37 | -0.37 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26.3 | Sat | WE | On | OFF | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27.3 | Sat | WE | On | OFF | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.1 | Sat | WE | On | OFF | 22 | 22.51 | -0.51 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.4 | Sat | WE | On | OFF | 22 | 22.44 | -0.44 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 26 | Sat | WE | Off | OFF | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25.1 | Sat | WE | Off | OFF | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.4 | Sat | WE | Off | OFF | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 21.2 | Sat | WE | Off | OFF | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 23:00 | 19.2 | Sat | WE | Off | OFF | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
Sun, 26/Jun | 24:00 | 18 | Sun | WE | Off | OFF | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 1:00 | 17.3 | Sun | WE | Off | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 2:00 | 16.3 | Sun | WE | Off | OFF | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 3:00 | 15.1 | Sun | WE | Off | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 4:00 | 15 | Sun | WE | Off | OFF | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 5:00 | 14.5 | Sun | WE | Off | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 6:00 | 14.4 | Sun | WE | Off | OFF | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 7:00 | 14.2 | Sun | WE | On | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 8:00 | 15.4 | Sun | WE | On | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 9:00 | 17.1 | Sun | WE | On | OFF | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 10:00 | 19.1 | Sun | WE | On | OFF | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 11:00 | 20.3 | Sun | WE | On | OFF | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 12:00 | 20.9 | Sun | WE | On | OFF | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 13:00 | 22.8 | Sun | WE | On | OFF | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 22.5 | Sun | WE | On | OFF | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 22.7 | Sun | WE | On | OFF | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23.4 | Sun | WE | On | OFF | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 22.3 | Sun | WE | On | OFF | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.1 | Sun | WE | On | OFF | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.3 | Sun | WE | Off | OFF | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 21.7 | Sun | WE | Off | OFF | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 21:00 | 20.6 | Sun | WE | Off | OFF | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 22:00 | 19.9 | Sun | WE | Off | OFF | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 23:00 | 18.5 | Sun | WE | Off | OFF | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
Mon, 27/Jun | 24:00 | 17.5 | Mon | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 1:00 | 17.1 | Mon | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 2:00 | 16.9 | Mon | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 3:00 | 16.5 | Mon | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 4:00 | 16.4 | Mon | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 5:00 | 15.8 | Mon | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 6:00 | 15.3 | Mon | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 7:00 | 14.3 | Mon | School Day | On | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 8:00 | 14.8 | Mon | School Day | On | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 9:00 | 15 | Mon | School Day | On | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 10:00 | 15.6 | Mon | School Day | On | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 11:00 | 17.4 | Mon | School Day | On | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 12:00 | 19 | Mon | School Day | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 13:00 | 19.8 | Mon | School Day | On | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 14:00 | 19.9 | Mon | School Day | On | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 15:00 | 17.3 | Mon | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 16:00 | 17.3 | Mon | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 17:00 | 17.7 | Mon | School Day | On | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 18:00 | 19 | Mon | School Day | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 19:00 | 17.9 | Mon | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 20:00 | 17.2 | Mon | School Day | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 21:00 | 16.5 | Mon | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 22:00 | 16.7 | Mon | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 23:00 | 16.2 | Mon | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
Tue, 28/Jun | 24:00 | 15.2 | Tue | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 1:00 | 14.2 | Tue | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 2:00 | 13.3 | Tue | School Day | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 3:00 | 12.8 | Tue | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 4:00 | 11.4 | Tue | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 5:00 | 10 | Tue | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 6:00 | 10.4 | Tue | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 7:00 | 10.2 | Tue | School Day | On | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 8:00 | 11.9 | Tue | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 9:00 | 14 | Tue | School Day | On | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 10:00 | 15.5 | Tue | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 11:00 | 17.1 | Tue | School Day | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 12:00 | 19.6 | Tue | School Day | On | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 13:00 | 17.7 | Tue | School Day | On | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 14:00 | 17.4 | Tue | School Day | On | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 15:00 | 15.5 | Tue | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 16:00 | 15.5 | Tue | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 17:00 | 16.6 | Tue | School Day | On | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 18:00 | 17.2 | Tue | School Day | On | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 19:00 | 17.4 | Tue | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 20:00 | 17.3 | Tue | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 21:00 | 17.5 | Tue | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 22:00 | 17.4 | Tue | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 23:00 | 17.5 | Tue | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
Wed, 29/Jun | 24:00 | 17 | Wed | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 1:00 | 17 | Wed | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 2:00 | 17 | Wed | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 3:00 | 16.4 | Wed | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 4:00 | 16.5 | Wed | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 5:00 | 16.6 | Wed | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 6:00 | 16.3 | Wed | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 7:00 | 15.7 | Wed | School Day | On | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 8:00 | 15.9 | Wed | School Day | On | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 9:00 | 16.3 | Wed | School Day | On | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 10:00 | 14.1 | Wed | School Day | On | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 11:00 | 12.6 | Wed | School Day | On | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 12:00 | 12.2 | Wed | School Day | On | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 13:00 | 11.7 | Wed | School Day | On | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 14:00 | 13 | Wed | School Day | On | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 15:00 | 14.4 | Wed | School Day | On | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 16:00 | 16 | Wed | School Day | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 17:00 | 17.3 | Wed | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 18:00 | 18.2 | Wed | School Day | On | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 19:00 | 18.9 | Wed | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 20:00 | 19.6 | Wed | School Day | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 21:00 | 19.9 | Wed | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 22:00 | 18.9 | Wed | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 23:00 | 17.5 | Wed | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
Thu, 30/Jun | 24:00 | 15.2 | Thu | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 1:00 | 14.3 | Thu | School Day | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 2:00 | 13.2 | Thu | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 3:00 | 13 | Thu | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 4:00 | 13 | Thu | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 5:00 | 12.4 | Thu | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 6:00 | 12.2 | Thu | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 7:00 | 12 | Thu | School Day | On | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 8:00 | 12.9 | Thu | School Day | On | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 9:00 | 14.5 | Thu | School Day | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 10:00 | 16.7 | Thu | School Day | On | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 11:00 | 17.9 | Thu | School Day | On | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 12:00 | 19.1 | Thu | School Day | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 13:00 | 20.2 | Thu | School Day | On | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 14:00 | 21.6 | Thu | School Day | On | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 15:00 | 21.7 | Thu | School Day | On | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 16:00 | 21.4 | Thu | School Day | On | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 17:00 | 20.7 | Thu | School Day | On | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 18:00 | 19.6 | Thu | School Day | On | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 19:00 | 19.5 | Thu | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 20:00 | 19.4 | Thu | School Day | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 21:00 | 18.8 | Thu | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 22:00 | 18.3 | Thu | School Day | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 23:00 | 17 | Thu | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
Fri, 01/Jul | 24:00 | 16.3 | Fri | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 1:00 | 16 | Fri | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 2:00 | 16.1 | Fri | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 3:00 | 16.2 | Fri | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 4:00 | 16.6 | Fri | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 5:00 | 16.5 | Fri | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 6:00 | 17 | Fri | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 7:00 | 17.3 | Fri | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 8:00 | 17.5 | Fri | School Day | On | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 9:00 | 18 | Fri | School Day | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 10:00 | 18.6 | Fri | School Day | On | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 11:00 | 20.2 | Fri | School Day | On | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 12:00 | 18.8 | Fri | School Day | On | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 13:00 | 22.4 | Fri | School Day | On | Off | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 21.9 | Fri | School Day | On | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 15:00 | 21.5 | Fri | School Day | On | Off | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 16:00 | 21 | Fri | School Day | On | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 17:00 | 20.1 | Fri | School Day | On | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 18:00 | 19.2 | Fri | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 19:00 | 19.5 | Fri | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 20:00 | 20.1 | Fri | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 21:00 | 20 | Fri | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 22:00 | 19.1 | Fri | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 23:00 | 18.2 | Fri | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
Sat, 02/Jul | 24:00 | 17.6 | Sat | WE | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 1:00 | 16.1 | Sat | WE | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 2:00 | 15.6 | Sat | WE | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 3:00 | 14.9 | Sat | WE | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 4:00 | 13.5 | Sat | WE | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 5:00 | 12.8 | Sat | WE | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 6:00 | 12.4 | Sat | WE | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 7:00 | 11.9 | Sat | WE | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 8:00 | 13.4 | Sat | WE | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 9:00 | 14.6 | Sat | WE | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 10:00 | 16.2 | Sat | WE | On | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 11:00 | 17.1 | Sat | WE | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 12:00 | 17.6 | Sat | WE | On | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 13:00 | 18 | Sat | WE | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 14:00 | 18.5 | Sat | WE | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 15:00 | 19.4 | Sat | WE | On | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 16:00 | 20 | Sat | WE | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 17:00 | 19.4 | Sat | WE | On | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 18:00 | 20 | Sat | WE | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 19:00 | 20.7 | Sat | WE | Off | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 20:00 | 20.5 | Sat | WE | Off | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 21:00 | 20.5 | Sat | WE | Off | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 22:00 | 19.4 | Sat | WE | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 23:00 | 18.2 | Sat | WE | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
Sun, 03/Jul | 24:00 | 16.8 | Sun | WE | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 1:00 | 15.5 | Sun | WE | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 2:00 | 15.3 | Sun | WE | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 3:00 | 14.4 | Sun | WE | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 4:00 | 13.4 | Sun | WE | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 5:00 | 12.6 | Sun | WE | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 6:00 | 12 | Sun | WE | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 7:00 | 12.2 | Sun | WE | On | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 8:00 | 13.8 | Sun | WE | On | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 9:00 | 15.8 | Sun | WE | On | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 10:00 | 17.6 | Sun | WE | On | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 11:00 | 19.2 | Sun | WE | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 12:00 | 21.2 | Sun | WE | On | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 13:00 | 21.9 | Sun | WE | On | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 14:00 | 22.5 | Sun | WE | On | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 22.5 | Sun | WE | On | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 24.5 | Sun | WE | On | Off | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23.8 | Sun | WE | On | Off | 22 | 22.18 | -0.18 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 24 | Sun | WE | On | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 23.5 | Sun | WE | Off | Off | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 23.2 | Sun | WE | Off | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 22.4 | Sun | WE | Off | Off | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 21.1 | Sun | WE | Off | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 23:00 | 18.8 | Sun | WE | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
Mon, 04/Jul | 24:00 | 18.2 | Mon | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 1:00 | 17.9 | Mon | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 2:00 | 16.6 | Mon | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 3:00 | 15.4 | Mon | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 4:00 | 14.7 | Mon | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 5:00 | 13.9 | Mon | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 6:00 | 13.2 | Mon | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 7:00 | 13.5 | Mon | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 8:00 | 14.9 | Mon | School Day | On | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 9:00 | 17.3 | Mon | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 10:00 | 19.5 | Mon | School Day | On | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 11:00 | 21.8 | Mon | School Day | On | Off | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0
| 12:00 | 23.2 | Mon | School Day | On | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 23.7 | Mon | School Day | On | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 24.4 | Mon | School Day | On | Off | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 25.9 | Mon | School Day | On | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26 | Mon | School Day | On | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.9 | Mon | School Day | On | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.9 | Mon | School Day | On | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.5 | Mon | School Day | Off | Off | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.3 | Mon | School Day | Off | Off | 22 | 22.23 | -0.23 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.8 | Mon | School Day | Off | Off | 22 | 22.18 | -0.18 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.3 | Mon | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.2 | Mon | School Day | Off | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
Tue, 05/Jul | 24:00 | 19.5 | Tue | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 1:00 | 18.3 | Tue | School Day | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 2:00 | 17.5 | Tue | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 3:00 | 16.7 | Tue | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 4:00 | 16.1 | Tue | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 5:00 | 15.6 | Tue | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 6:00 | 15.4 | Tue | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 7:00 | 15.2 | Tue | School Day | On | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 8:00 | 16.6 | Tue | School Day | On | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 9:00 | 18.6 | Tue | School Day | On | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 10:00 | 20.7 | Tue | School Day | On | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 11:00 | 23.2 | Tue | School Day | On | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 24.7 | Tue | School Day | On | Off | 22 | 22.27 | -0.27 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 26.1 | Tue | School Day | On | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 27.3 | Tue | School Day | On | Off | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 28.5 | Tue | School Day | On | Off | 22 | 22.65 | -0.65 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 29.2 | Tue | School Day | On | Off | 22 | 22.72 | -0.72 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 29 | Tue | School Day | On | Off | 22 | 22.7 | -0.7 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 28.6 | Tue | School Day | On | Off | 22 | 22.66 | -0.66 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 28.4 | Tue | School Day | Off | Off | 22 | 22.64 | -0.64 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 27.4 | Tue | School Day | Off | Off | 22 | 22.54 | -0.54 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 25.7 | Tue | School Day | Off | Off | 22 | 22.37 | -0.37 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 24.2 | Tue | School Day | Off | Off | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 23 | Tue | School Day | Off | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Wed, 06/Jul | 24:00 | 21.6 | Wed | School Day | Off | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 1:00 | 20.5 | Wed | School Day | Off | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 2:00 | 19.6 | Wed | School Day | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 3:00 | 19 | Wed | School Day | Off | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 4:00 | 18.5 | Wed | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 5:00 | 18.1 | Wed | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 6:00 | 18.1 | Wed | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 7:00 | 18 | Wed | School Day | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 8:00 | 18.9 | Wed | School Day | On | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 9:00 | 20.1 | Wed | School Day | On | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 10:00 | 21.8 | Wed | School Day | On | Off | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0
| 11:00 | 23.4 | Wed | School Day | On | Off | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25.1 | Wed | School Day | On | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 27.2 | Wed | School Day | On | Off | 22 | 22.52 | -0.52 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 29.1 | Wed | School Day | On | Off | 22 | 22.71 | -0.71 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 30.7 | Wed | School Day | On | Off | 22 | 22.87 | -0.87 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 30.7 | Wed | School Day | On | Off | 22 | 22.87 | -0.87 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 30.6 | Wed | School Day | On | Off | 22 | 22.86 | -0.86 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 29.9 | Wed | School Day | On | Off | 22 | 22.79 | -0.79 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 29.2 | Wed | School Day | Off | Off | 22 | 22.72 | -0.72 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 28 | Wed | School Day | Off | Off | 22 | 22.6 | -0.6 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 27.5 | Wed | School Day | Off | Off | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 26.8 | Wed | School Day | Off | Off | 22 | 22.48 | -0.48 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 25.9 | Wed | School Day | Off | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Thu, 07/Jul | 24:00 | 25.2 | Thu | School Day | Off | Off | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 24.4 | Thu | School Day | Off | Off | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 2:00 | 23.1 | Thu | School Day | Off | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 3:00 | 22.8 | Thu | School Day | Off | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 4:00 | 20.3 | Thu | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 5:00 | 19.4 | Thu | School Day | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 6:00 | 19.3 | Thu | School Day | Off | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 7:00 | 19.6 | Thu | School Day | On | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 8:00 | 20.1 | Thu | School Day | On | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 9:00 | 20.5 | Thu | School Day | On | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 10:00 | 20.8 | Thu | School Day | On | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 11:00 | 20.6 | Thu | School Day | On | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 12:00 | 20.9 | Thu | School Day | On | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 13:00 | 21.4 | Thu | School Day | On | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 14:00 | 21.6 | Thu | School Day | On | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 15:00 | 21.3 | Thu | School Day | On | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 16:00 | 20.8 | Thu | School Day | On | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 17:00 | 21.6 | Thu | School Day | On | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 18:00 | 20.1 | Thu | School Day | On | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 19:00 | 20.1 | Thu | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 20:00 | 20.2 | Thu | School Day | Off | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 21:00 | 19.7 | Thu | School Day | Off | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 22:00 | 19.5 | Thu | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 23:00 | 19.2 | Thu | School Day | Off | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
Fri, 08/Jul | 24:00 | 18.9 | Fri | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 1:00 | 18.6 | Fri | School Day | Off | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 2:00 | 17.9 | Fri | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 3:00 | 17 | Fri | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 4:00 | 17.2 | Fri | School Day | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 5:00 | 17.5 | Fri | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 6:00 | 17.5 | Fri | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 7:00 | 17.8 | Fri | School Day | On | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 8:00 | 17.9 | Fri | School Day | On | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 9:00 | 18.4 | Fri | School Day | On | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 10:00 | 19.2 | Fri | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 11:00 | 19.8 | Fri | School Day | On | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 12:00 | 21.3 | Fri | School Day | On | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 13:00 | 22.2 | Fri | School Day | On | Off | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 22.6 | Fri | School Day | On | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.3 | Fri | School Day | On | Off | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 25.6 | Fri | School Day | On | Off | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 22.3 | Fri | School Day | On | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.4 | Fri | School Day | On | Off | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.9 | Fri | School Day | Off | Off | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 21 | Fri | School Day | Off | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 21:00 | 19.8 | Fri | School Day | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 22:00 | 19.5 | Fri | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 23:00 | 19.7 | Fri | School Day | Off | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
Sat, 09/Jul | 24:00 | 17.9 | Sat | WE | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 1:00 | 17.9 | Sat | WE | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 2:00 | 18.4 | Sat | WE | Off | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 3:00 | 17.8 | Sat | WE | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 4:00 | 17.3 | Sat | WE | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 5:00 | 16.9 | Sat | WE | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 6:00 | 16.5 | Sat | WE | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 7:00 | 16.5 | Sat | WE | On | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 8:00 | 16.4 | Sat | WE | On | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 9:00 | 16.5 | Sat | WE | On | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 10:00 | 17 | Sat | WE | On | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 11:00 | 18 | Sat | WE | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 12:00 | 18 | Sat | WE | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 13:00 | 18.5 | Sat | WE | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 14:00 | 18.6 | Sat | WE | On | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 15:00 | 19 | Sat | WE | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 16:00 | 19.2 | Sat | WE | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 17:00 | 18.6 | Sat | WE | On | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 18:00 | 17.8 | Sat | WE | On | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 19:00 | 17.8 | Sat | WE | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 20:00 | 18 | Sat | WE | Off | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 21:00 | 17.8 | Sat | WE | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 22:00 | 17.2 | Sat | WE | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 23:00 | 16.3 | Sat | WE | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
Sun, 10/Jul | 24:00 | 16.1 | Sun | WE | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 1:00 | 15.8 | Sun | WE | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 2:00 | 15.8 | Sun | WE | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 3:00 | 15.7 | Sun | WE | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 4:00 | 15.6 | Sun | WE | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 5:00 | 15.7 | Sun | WE | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 6:00 | 15.4 | Sun | WE | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 7:00 | 15.6 | Sun | WE | On | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 8:00 | 15.9 | Sun | WE | On | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 9:00 | 16.6 | Sun | WE | On | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 10:00 | 18 | Sun | WE | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 11:00 | 18.7 | Sun | WE | On | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 12:00 | 20.1 | Sun | WE | On | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 13:00 | 21.4 | Sun | WE | On | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 14:00 | 23.4 | Sun | WE | On | Off | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 24.1 | Sun | WE | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23.6 | Sun | WE | On | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 24.5 | Sun | WE | On | Off | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 24.4 | Sun | WE | On | Off | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 24.7 | Sun | WE | Off | Off | 22 | 22.27 | -0.27 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.6 | Sun | WE | Off | Off | 22 | 22.26 | -0.26 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24 | Sun | WE | Off | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23 | Sun | WE | Off | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 22.1 | Sun | WE | Off | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Mon, 11/Jul | 24:00 | 21.7 | Mon | School Day | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 1:00 | 21.1 | Mon | School Day | Off | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 2:00 | 20.1 | Mon | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 3:00 | 18.9 | Mon | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 4:00 | 17.9 | Mon | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 5:00 | 17.6 | Mon | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 6:00 | 18.2 | Mon | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 7:00 | 18 | Mon | School Day | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 8:00 | 18.7 | Mon | School Day | On | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 9:00 | 19.1 | Mon | School Day | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 10:00 | 19.7 | Mon | School Day | On | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 11:00 | 21.1 | Mon | School Day | On | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 12:00 | 22.1 | Mon | School Day | On | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 22.5 | Mon | School Day | On | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 24.1 | Mon | School Day | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 25 | Mon | School Day | On | Off | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 25.2 | Mon | School Day | On | Off | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26.4 | Mon | School Day | On | Off | 22 | 22.44 | -0.44 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.6 | Mon | School Day | On | Off | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 26.8 | Mon | School Day | Off | Off | 22 | 22.48 | -0.48 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 26.5 | Mon | School Day | Off | Off | 22 | 22.45 | -0.45 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 25.6 | Mon | School Day | Off | Off | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 24.8 | Mon | School Day | Off | Off | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 23.6 | Mon | School Day | Off | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Tue, 12/Jul | 24:00 | 21.1 | Tue | School Day | Off | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 1:00 | 20.7 | Tue | School Day | Off | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 2:00 | 18.5 | Tue | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 3:00 | 17.5 | Tue | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 4:00 | 18.3 | Tue | School Day | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 5:00 | 16.5 | Tue | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 6:00 | 16.5 | Tue | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 7:00 | 16.1 | Tue | School Day | On | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 8:00 | 16.6 | Tue | School Day | On | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 9:00 | 17.8 | Tue | School Day | On | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 10:00 | 20 | Tue | School Day | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 11:00 | 21.6 | Tue | School Day | On | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 12:00 | 21.9 | Tue | School Day | On | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 13:00 | 21.7 | Tue | School Day | On | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 14:00 | 22.1 | Tue | School Day | On | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 22.1 | Tue | School Day | On | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 22.7 | Tue | School Day | On | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 22.8 | Tue | School Day | On | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.7 | Tue | School Day | On | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 23.1 | Tue | School Day | Off | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 22.9 | Tue | School Day | Off | Off | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 22.3 | Tue | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 20.8 | Tue | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 23:00 | 18.7 | Tue | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
Wed, 13/Jul | 24:00 | 17.7 | Wed | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 1:00 | 16.3 | Wed | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 2:00 | 16 | Wed | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 3:00 | 14.6 | Wed | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 4:00 | 15.1 | Wed | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 5:00 | 13.6 | Wed | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 6:00 | 14.8 | Wed | School Day | Off | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 7:00 | 15.9 | Wed | School Day | On | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 8:00 | 16.7 | Wed | School Day | On | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 9:00 | 19 | Wed | School Day | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 10:00 | 19.5 | Wed | School Day | On | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 11:00 | 20.5 | Wed | School Day | On | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 12:00 | 22.1 | Wed | School Day | On | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 22.7 | Wed | School Day | On | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 23.6 | Wed | School Day | On | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 24 | Wed | School Day | On | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 24.6 | Wed | School Day | On | Off | 22 | 22.26 | -0.26 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.3 | Wed | School Day | On | Off | 22 | 22.33 | -0.33 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.6 | Wed | School Day | On | Off | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25 | Wed | School Day | Off | Off | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24 | Wed | School Day | Off | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.1 | Wed | School Day | Off | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 21 | Wed | School Day | Off | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 23:00 | 19.4 | Wed | School Day | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
Thu, 14/Jul | 24:00 | 17.7 | Thu | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 1:00 | 16.4 | Thu | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 2:00 | 15.6 | Thu | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 3:00 | 14.3 | Thu | School Day | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 4:00 | 13.5 | Thu | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 5:00 | 13.7 | Thu | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 6:00 | 13 | Thu | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 7:00 | 13.5 | Thu | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 8:00 | 14 | Thu | School Day | On | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 9:00 | 15.5 | Thu | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 10:00 | 16.6 | Thu | School Day | On | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 11:00 | 17.8 | Thu | School Day | On | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 12:00 | 18.6 | Thu | School Day | On | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 13:00 | 19.2 | Thu | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 14:00 | 20.5 | Thu | School Day | On | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 15:00 | 22.3 | Thu | School Day | On | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 22 | Thu | School Day | On | Off | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23 | Thu | School Day | On | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.6 | Thu | School Day | On | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.9 | Thu | School Day | Off | Off | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 23 | Thu | School Day | Off | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 22.6 | Thu | School Day | Off | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 21.4 | Thu | School Day | Off | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 23:00 | 19.6 | Thu | School Day | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
Fri, 15/Jul | 24:00 | 18.5 | Fri | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 1:00 | 17.1 | Fri | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 2:00 | 16 | Fri | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 3:00 | 15.1 | Fri | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 4:00 | 13.6 | Fri | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 5:00 | 12.9 | Fri | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 6:00 | 12.9 | Fri | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 7:00 | 13.5 | Fri | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 8:00 | 15.1 | Fri | School Day | On | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 9:00 | 16.6 | Fri | School Day | On | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 10:00 | 18 | Fri | School Day | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 11:00 | 20 | Fri | School Day | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 12:00 | 21.8 | Fri | School Day | On | Off | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0
| 13:00 | 23.3 | Fri | School Day | On | Off | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 25.1 | Fri | School Day | On | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26 | Fri | School Day | On | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26.2 | Fri | School Day | On | Off | 22 | 22.42 | -0.42 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.8 | Fri | School Day | On | Off | 22 | 22.58 | -0.58 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 28.8 | Fri | School Day | On | Off | 22 | 22.68 | -0.68 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 28.7 | Fri | School Day | Off | Off | 22 | 22.67 | -0.67 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 28.3 | Fri | School Day | Off | Off | 22 | 22.63 | -0.63 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 27.7 | Fri | School Day | Off | Off | 22 | 22.57 | -0.57 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 26.1 | Fri | School Day | Off | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 24.1 | Fri | School Day | Off | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Sat, 16/Jul | 24:00 | 21.7 | Sat | WE | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 1:00 | 20 | Sat | WE | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 2:00 | 20.3 | Sat | WE | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 3:00 | 20 | Sat | WE | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 4:00 | 18.4 | Sat | WE | Off | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 5:00 | 17.8 | Sat | WE | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 6:00 | 16.7 | Sat | WE | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 7:00 | 16.7 | Sat | WE | On | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 8:00 | 17.1 | Sat | WE | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 9:00 | 17.1 | Sat | WE | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 10:00 | 18.5 | Sat | WE | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 11:00 | 18.8 | Sat | WE | On | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 12:00 | 19.6 | Sat | WE | On | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 13:00 | 20.4 | Sat | WE | On | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 14:00 | 20.5 | Sat | WE | On | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 15:00 | 21.9 | Sat | WE | On | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 16:00 | 23.6 | Sat | WE | On | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 24.6 | Sat | WE | On | Off | 22 | 22.26 | -0.26 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.3 | Sat | WE | On | Off | 22 | 22.33 | -0.33 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.1 | Sat | WE | Off | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.3 | Sat | WE | Off | Off | 22 | 22.23 | -0.23 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 22.9 | Sat | WE | Off | Off | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 21.1 | Sat | WE | Off | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 23:00 | 20.1 | Sat | WE | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
Sun, 17/Jul | 24:00 | 19.1 | Sun | WE | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 1:00 | 19 | Sun | WE | Off | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 2:00 | 18 | Sun | WE | Off | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 3:00 | 17.2 | Sun | WE | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 4:00 | 16.6 | Sun | WE | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 5:00 | 15.9 | Sun | WE | Off | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 6:00 | 15.5 | Sun | WE | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 7:00 | 15.1 | Sun | WE | On | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 8:00 | 16 | Sun | WE | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 9:00 | 17.2 | Sun | WE | On | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 10:00 | 19.5 | Sun | WE | On | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 11:00 | 21.7 | Sun | WE | On | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 12:00 | 22.8 | Sun | WE | On | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 25.1 | Sun | WE | On | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 27 | Sun | WE | On | Off | 22 | 22.5 | -0.5 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26.8 | Sun | WE | On | Off | 22 | 22.48 | -0.48 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 29 | Sun | WE | On | Off | 22 | 22.7 | -0.7 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 28.7 | Sun | WE | On | Off | 22 | 22.67 | -0.67 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 27.8 | Sun | WE | On | Off | 22 | 22.58 | -0.58 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 28.5 | Sun | WE | Off | Off | 22 | 22.65 | -0.65 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 28.3 | Sun | WE | Off | Off | 22 | 22.63 | -0.63 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 27.6 | Sun | WE | Off | Off | 22 | 22.56 | -0.56 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 26.8 | Sun | WE | Off | Off | 22 | 22.48 | -0.48 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 25.5 | Sun | WE | Off | Off | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Mon, 18/Jul | 24:00 | 23.7 | Mon | School Day | Off | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 22.6 | Mon | School Day | Off | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 2:00 | 20.8 | Mon | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 3:00 | 19.5 | Mon | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 4:00 | 18 | Mon | School Day | Off | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 5:00 | 17.3 | Mon | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 6:00 | 16 | Mon | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 7:00 | 15.6 | Mon | School Day | On | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 8:00 | 16 | Mon | School Day | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 9:00 | 18 | Mon | School Day | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 10:00 | 19.7 | Mon | School Day | On | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 11:00 | 20.8 | Mon | School Day | On | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 12:00 | 22.7 | Mon | School Day | On | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 23.6 | Mon | School Day | On | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 23.5 | Mon | School Day | On | Off | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.9 | Mon | School Day | On | Off | 22 | 22.19 | -0.19 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 25 | Mon | School Day | On | Off | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26 | Mon | School Day | On | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.2 | Mon | School Day | On | Off | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.1 | Mon | School Day | Off | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.3 | Mon | School Day | Off | Off | 22 | 22.23 | -0.23 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.5 | Mon | School Day | Off | Off | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.2 | Mon | School Day | Off | Off | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 20.8 | Mon | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
Tue, 19/Jul | 24:00 | 19.1 | Tue | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 1:00 | 18.5 | Tue | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 2:00 | 17 | Tue | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 3:00 | 16.2 | Tue | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 4:00 | 15.5 | Tue | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 5:00 | 15.8 | Tue | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 6:00 | 14.9 | Tue | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 7:00 | 14.9 | Tue | School Day | On | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 8:00 | 15.8 | Tue | School Day | On | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 9:00 | 17.3 | Tue | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 10:00 | 19.1 | Tue | School Day | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 11:00 | 20.7 | Tue | School Day | On | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 12:00 | 22.3 | Tue | School Day | On | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 24.1 | Tue | School Day | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 24.7 | Tue | School Day | On | Off | 22 | 22.27 | -0.27 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26.1 | Tue | School Day | On | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27.2 | Tue | School Day | On | Off | 22 | 22.52 | -0.52 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.6 | Tue | School Day | On | Off | 22 | 22.56 | -0.56 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 27.6 | Tue | School Day | On | Off | 22 | 22.56 | -0.56 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 27.4 | Tue | School Day | Off | Off | 22 | 22.54 | -0.54 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 27.4 | Tue | School Day | Off | Off | 22 | 22.54 | -0.54 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 26.8 | Tue | School Day | Off | Off | 22 | 22.48 | -0.48 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23.4 | Tue | School Day | Off | Off | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.7 | Tue | School Day | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
Wed, 20/Jul | 24:00 | 20.5 | Wed | School Day | Off | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 1:00 | 19.3 | Wed | School Day | Off | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 2:00 | 18.6 | Wed | School Day | Off | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 3:00 | 18.1 | Wed | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 4:00 | 17.9 | Wed | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 5:00 | 17.3 | Wed | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 6:00 | 16.7 | Wed | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 7:00 | 16.8 | Wed | School Day | On | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 8:00 | 17.9 | Wed | School Day | On | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 9:00 | 19.7 | Wed | School Day | On | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 10:00 | 21.6 | Wed | School Day | On | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 11:00 | 24.1 | Wed | School Day | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25.6 | Wed | School Day | On | Off | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 27.5 | Wed | School Day | On | Off | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 28.6 | Wed | School Day | On | Off | 22 | 22.66 | -0.66 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 29.1 | Wed | School Day | On | Off | 22 | 22.71 | -0.71 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 30.3 | Wed | School Day | On | Off | 22 | 22.83 | -0.83 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 30.6 | Wed | School Day | On | Off | 22 | 22.86 | -0.86 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 29.9 | Wed | School Day | On | Off | 22 | 22.79 | -0.79 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 29 | Wed | School Day | Off | Off | 22 | 22.7 | -0.7 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 28.2 | Wed | School Day | Off | Off | 22 | 22.62 | -0.62 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 26.4 | Wed | School Day | Off | Off | 22 | 22.44 | -0.44 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23.7 | Wed | School Day | Off | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 22 | Wed | School Day | Off | Off | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Thu, 21/Jul | 24:00 | 21.1 | Thu | School Day | Off | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 1:00 | 20.9 | Thu | School Day | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 2:00 | 20.4 | Thu | School Day | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 3:00 | 19.9 | Thu | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 4:00 | 19.6 | Thu | School Day | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 5:00 | 19.1 | Thu | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 6:00 | 18.3 | Thu | School Day | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 7:00 | 19.1 | Thu | School Day | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 8:00 | 20 | Thu | School Day | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 9:00 | 20.6 | Thu | School Day | On | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 10:00 | 21.6 | Thu | School Day | On | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 11:00 | 24.1 | Thu | School Day | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25.6 | Thu | School Day | On | Off | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 28.6 | Thu | School Day | On | Off | 22 | 22.66 | -0.66 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 30.6 | Thu | School Day | On | Off | 22 | 22.86 | -0.86 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 31 | Thu | School Day | On | Off | 22 | 22.9 | -0.9 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 32.1 | Thu | School Day | On | Off | 22 | 23.01 | -1.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 32.2 | Thu | School Day | On | Off | 22 | 23.02 | -1.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 32.6 | Thu | School Day | On | Off | 22 | 23.06 | -1.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 31.7 | Thu | School Day | Off | Off | 22 | 22.97 | -0.97 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 31 | Thu | School Day | Off | Off | 22 | 22.9 | -0.9 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 26.9 | Thu | School Day | Off | Off | 22 | 22.49 | -0.49 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 25.6 | Thu | School Day | Off | Off | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 24.7 | Thu | School Day | Off | Off | 22 | 22.27 | -0.27 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Fri, 22/Jul | 24:00 | 22.9 | Fri | School Day | Off | Off | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 22 | Fri | School Day | Off | Off | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 2:00 | 21.7 | Fri | School Day | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 3:00 | 21.9 | Fri | School Day | Off | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 4:00 | 21.4 | Fri | School Day | Off | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 5:00 | 21.2 | Fri | School Day | Off | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 6:00 | 21.3 | Fri | School Day | Off | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 7:00 | 21.5 | Fri | School Day | On | Off | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 8:00 | 21.5 | Fri | School Day | On | Off | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 9:00 | 22.6 | Fri | School Day | On | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 10:00 | 24.9 | Fri | School Day | On | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 11:00 | 27.4 | Fri | School Day | On | Off | 22 | 22.54 | -0.54 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 29.7 | Fri | School Day | On | Off | 22 | 22.77 | -0.77 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 31.2 | Fri | School Day | On | Off | 22 | 22.92 | -0.92 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 32.7 | Fri | School Day | On | Off | 22 | 23.07 | -1.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 33.3 | Fri | School Day | On | Off | 22 | 23.13 | -1.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 34.1 | Fri | School Day | On | Off | 22 | 23.21 | -1.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 34 | Fri | School Day | On | Off | 22 | 23.2 | -1.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 34.6 | Fri | School Day | On | Off | 22 | 23.26 | -1.26 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 33.7 | Fri | School Day | Off | Off | 22 | 23.17 | -1.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 32.7 | Fri | School Day | Off | Off | 22 | 23.07 | -1.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 31.6 | Fri | School Day | Off | Off | 22 | 22.96 | -0.96 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 29.2 | Fri | School Day | Off | Off | 22 | 22.72 | -0.72 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 27.7 | Fri | School Day | Off | Off | 22 | 22.57 | -0.57 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Sat, 23/Jul | 24:00 | 27.3 | Sat | WE | Off | Off | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 23.9 | Sat | WE | Off | Off | 22 | 22.19 | -0.19 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 2:00 | 22.9 | Sat | WE | Off | Off | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 3:00 | 21.7 | Sat | WE | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 4:00 | 21 | Sat | WE | Off | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 5:00 | 21 | Sat | WE | Off | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 6:00 | 20.7 | Sat | WE | Off | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 7:00 | 20.6 | Sat | WE | On | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 8:00 | 21.4 | Sat | WE | On | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 9:00 | 21.8 | Sat | WE | On | Off | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0
| 10:00 | 23 | Sat | WE | On | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 11:00 | 24.4 | Sat | WE | On | Off | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 26.3 | Sat | WE | On | Off | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 28.3 | Sat | WE | On | Off | 22 | 22.63 | -0.63 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 30.1 | Sat | WE | On | Off | 22 | 22.81 | -0.81 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 30.3 | Sat | WE | On | Off | 22 | 22.83 | -0.83 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 31.8 | Sat | WE | On | Off | 22 | 22.98 | -0.98 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 31.8 | Sat | WE | On | Off | 22 | 22.98 | -0.98 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 32.1 | Sat | WE | On | Off | 22 | 23.01 | -1.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 32 | Sat | WE | Off | Off | 22 | 23 | -1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 31.6 | Sat | WE | Off | Off | 22 | 22.96 | -0.96 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 31.1 | Sat | WE | Off | Off | 22 | 22.91 | -0.91 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 30.3 | Sat | WE | Off | Off | 22 | 22.83 | -0.83 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 28.9 | Sat | WE | Off | Off | 22 | 22.69 | -0.69 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Sun, 24/Jul | 24:00 | 27.2 | Sun | WE | Off | Off | 22 | 22.52 | -0.52 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 26 | Sun | WE | Off | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 2:00 | 24.9 | Sun | WE | Off | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 3:00 | 23.8 | Sun | WE | Off | Off | 22 | 22.18 | -0.18 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 4:00 | 22.7 | Sun | WE | Off | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 5:00 | 21.6 | Sun | WE | Off | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 6:00 | 20.9 | Sun | WE | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 7:00 | 20.6 | Sun | WE | On | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 8:00 | 21 | Sun | WE | On | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 9:00 | 22.3 | Sun | WE | On | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 10:00 | 24 | Sun | WE | On | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 11:00 | 26 | Sun | WE | On | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 27.2 | Sun | WE | On | Off | 22 | 22.52 | -0.52 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 28.9 | Sun | WE | On | Off | 22 | 22.69 | -0.69 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 30 | Sun | WE | On | Off | 22 | 22.8 | -0.8 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 30.8 | Sun | WE | On | Off | 22 | 22.88 | -0.88 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 31 | Sun | WE | On | Off | 22 | 22.9 | -0.9 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 30.3 | Sun | WE | On | Off | 22 | 22.83 | -0.83 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 30.3 | Sun | WE | On | Off | 22 | 22.83 | -0.83 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 28.6 | Sun | WE | Off | Off | 22 | 22.66 | -0.66 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 28.2 | Sun | WE | Off | Off | 22 | 22.62 | -0.62 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 27.5 | Sun | WE | Off | Off | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 25.7 | Sun | WE | Off | Off | 22 | 22.37 | -0.37 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 24 | Sun | WE | Off | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Mon, 25/Jul | 24:00 | 22.3 | Mon | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 21.9 | Mon | School Day | Off | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 2:00 | 20.6 | Mon | School Day | Off | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 3:00 | 19.7 | Mon | School Day | Off | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 4:00 | 19 | Mon | School Day | Off | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 5:00 | 18.8 | Mon | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 6:00 | 18.8 | Mon | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 7:00 | 18.2 | Mon | School Day | On | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 8:00 | 19.2 | Mon | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 9:00 | 20.5 | Mon | School Day | On | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 10:00 | 22.5 | Mon | School Day | On | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 11:00 | 24 | Mon | School Day | On | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25.4 | Mon | School Day | On | Off | 22 | 22.34 | -0.34 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 26.6 | Mon | School Day | On | Off | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 28.2 | Mon | School Day | On | Off | 22 | 22.62 | -0.62 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 29 | Mon | School Day | On | Off | 22 | 22.7 | -0.7 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 30.3 | Mon | School Day | On | Off | 22 | 22.83 | -0.83 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 30.3 | Mon | School Day | On | Off | 22 | 22.83 | -0.83 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 30.6 | Mon | School Day | On | Off | 22 | 22.86 | -0.86 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 29 | Mon | School Day | Off | Off | 22 | 22.7 | -0.7 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 29 | Mon | School Day | Off | Off | 22 | 22.7 | -0.7 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 28.2 | Mon | School Day | Off | Off | 22 | 22.62 | -0.62 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 26.9 | Mon | School Day | Off | Off | 22 | 22.49 | -0.49 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 25.5 | Mon | School Day | Off | Off | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Tue, 26/Jul | 24:00 | 24.5 | Tue | School Day | Off | Off | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 22.2 | Tue | School Day | Off | Off | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 2:00 | 22.9 | Tue | School Day | Off | Off | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 3:00 | 21.7 | Tue | School Day | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 4:00 | 20.7 | Tue | School Day | Off | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 5:00 | 20.8 | Tue | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 6:00 | 20.4 | Tue | School Day | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 7:00 | 18.2 | Tue | School Day | On | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 8:00 | 19.1 | Tue | School Day | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 9:00 | 20 | Tue | School Day | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 10:00 | 21.6 | Tue | School Day | On | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 11:00 | 22.8 | Tue | School Day | On | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 24.1 | Tue | School Day | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 26 | Tue | School Day | On | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 25.6 | Tue | School Day | On | Off | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26.7 | Tue | School Day | On | Off | 22 | 22.47 | -0.47 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27.7 | Tue | School Day | On | Off | 22 | 22.57 | -0.57 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.9 | Tue | School Day | On | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.1 | Tue | School Day | On | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.1 | Tue | School Day | Off | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25 | Tue | School Day | Off | Off | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24.7 | Tue | School Day | Off | Off | 22 | 22.27 | -0.27 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23.2 | Tue | School Day | Off | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 22.1 | Tue | School Day | Off | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Wed, 27/Jul | 24:00 | 21.4 | Wed | School Day | Off | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 1:00 | 19.9 | Wed | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 2:00 | 18.2 | Wed | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 3:00 | 17 | Wed | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 4:00 | 16.4 | Wed | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 5:00 | 16.4 | Wed | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 6:00 | 15.1 | Wed | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 7:00 | 14.6 | Wed | School Day | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 8:00 | 15.1 | Wed | School Day | On | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 9:00 | 17 | Wed | School Day | On | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 10:00 | 19.1 | Wed | School Day | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 11:00 | 21.1 | Wed | School Day | On | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 12:00 | 23.1 | Wed | School Day | On | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 24.5 | Wed | School Day | On | Off | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 24.8 | Wed | School Day | On | Off | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 24.6 | Wed | School Day | On | Off | 22 | 22.26 | -0.26 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 25.8 | Wed | School Day | On | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26.6 | Wed | School Day | On | Off | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.2 | Wed | School Day | On | Off | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25 | Wed | School Day | Off | Off | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25.1 | Wed | School Day | Off | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.7 | Wed | School Day | Off | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.3 | Wed | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 20.9 | Wed | School Day | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
Thu, 28/Jul | 24:00 | 20 | Thu | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 1:00 | 18.2 | Thu | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 2:00 | 18.4 | Thu | School Day | Off | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 3:00 | 17.6 | Thu | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 4:00 | 15.1 | Thu | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 5:00 | 16.6 | Thu | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 6:00 | 15.9 | Thu | School Day | Off | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 7:00 | 16.3 | Thu | School Day | On | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 8:00 | 16.4 | Thu | School Day | On | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 9:00 | 18.1 | Thu | School Day | On | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 10:00 | 19.9 | Thu | School Day | On | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 11:00 | 21.4 | Thu | School Day | On | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 12:00 | 22.8 | Thu | School Day | On | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 24.7 | Thu | School Day | On | Off | 22 | 22.27 | -0.27 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 25.3 | Thu | School Day | On | Off | 22 | 22.33 | -0.33 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26.1 | Thu | School Day | On | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 25.9 | Thu | School Day | On | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.8 | Thu | School Day | On | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26 | Thu | School Day | On | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.9 | Thu | School Day | Off | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.8 | Thu | School Day | Off | Off | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24.1 | Thu | School Day | Off | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.7 | Thu | School Day | Off | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.1 | Thu | School Day | Off | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
Fri, 29/Jul | 24:00 | 20.4 | Fri | School Day | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 1:00 | 19.7 | Fri | School Day | Off | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 2:00 | 17.9 | Fri | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 3:00 | 16.6 | Fri | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 4:00 | 15.5 | Fri | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 5:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 6:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 7:00 | 15.7 | Fri | School Day | On | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 8:00 | 16.1 | Fri | School Day | On | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 9:00 | 17 | Fri | School Day | On | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 10:00 | 19.5 | Fri | School Day | On | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 11:00 | 21.1 | Fri | School Day | On | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 12:00 | 23.1 | Fri | School Day | On | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 25.2 | Fri | School Day | On | Off | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 25.8 | Fri | School Day | On | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27.1 | Fri | School Day | On | Off | 22 | 22.51 | -0.51 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27.1 | Fri | School Day | On | Off | 22 | 22.51 | -0.51 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.4 | Fri | School Day | On | Off | 22 | 22.34 | -0.34 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.5 | Fri | School Day | On | Off | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 26 | Fri | School Day | Off | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.5 | Fri | School Day | Off | Off | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.6 | Fri | School Day | Off | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.1 | Fri | School Day | Off | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 20.3 | Fri | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
Sat, 30/Jul | 24:00 | 20.6 | Sat | WE | Off | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 1:00 | 19.9 | Sat | WE | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 2:00 | 19.5 | Sat | WE | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 3:00 | 19.1 | Sat | WE | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 4:00 | 18.9 | Sat | WE | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 5:00 | 18.4 | Sat | WE | Off | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 6:00 | 17.8 | Sat | WE | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 7:00 | 18 | Sat | WE | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 8:00 | 18.3 | Sat | WE | On | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 9:00 | 18.4 | Sat | WE | On | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 10:00 | 18.7 | Sat | WE | On | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 11:00 | 18.1 | Sat | WE | On | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 12:00 | 18.1 | Sat | WE | On | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 13:00 | 19.1 | Sat | WE | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 14:00 | 18.6 | Sat | WE | On | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 15:00 | 19.6 | Sat | WE | On | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 16:00 | 17 | Sat | WE | On | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 17:00 | 17.7 | Sat | WE | On | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 18:00 | 18.5 | Sat | WE | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 19:00 | 19.6 | Sat | WE | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 20:00 | 18.9 | Sat | WE | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 21:00 | 19 | Sat | WE | Off | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 22:00 | 18.6 | Sat | WE | Off | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 23:00 | 17.7 | Sat | WE | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
Sun, 31/Jul | 24:00 | 16.4 | Sun | WE | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 1:00 | 15.5 | Sun | WE | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 2:00 | 14.9 | Sun | WE | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 3:00 | 14.5 | Sun | WE | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 4:00 | 13.5 | Sun | WE | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 5:00 | 13 | Sun | WE | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 6:00 | 12.7 | Sun | WE | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 7:00 | 12.4 | Sun | WE | On | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 8:00 | 13.3 | Sun | WE | On | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 9:00 | 14.6 | Sun | WE | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 10:00 | 16.1 | Sun | WE | On | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 11:00 | 17.3 | Sun | WE | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 12:00 | 18.3 | Sun | WE | On | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 13:00 | 18.4 | Sun | WE | On | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 14:00 | 19.5 | Sun | WE | On | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 15:00 | 19.1 | Sun | WE | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 16:00 | 19.1 | Sun | WE | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 17:00 | 18.8 | Sun | WE | On | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 18:00 | 18 | Sun | WE | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 19:00 | 17 | Sun | WE | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 20:00 | 16.7 | Sun | WE | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 21:00 | 16.7 | Sun | WE | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 22:00 | 15.7 | Sun | WE | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 23:00 | 14.5 | Sun | WE | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
Mon, 01/Aug | 24:00 | 13.5 | Mon | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 1:00 | 13.3 | Mon | School Day | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 2:00 | 12.6 | Mon | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 3:00 | 12.1 | Mon | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 4:00 | 11.9 | Mon | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 5:00 | 11.4 | Mon | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 6:00 | 11.4 | Mon | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 7:00 | 9.7 | Mon | School Day | On | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 8:00 | 11.7 | Mon | School Day | On | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 9:00 | 13.4 | Mon | School Day | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 10:00 | 15.2 | Mon | School Day | On | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 11:00 | 17.3 | Mon | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 12:00 | 18.7 | Mon | School Day | On | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 13:00 | 20.2 | Mon | School Day | On | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 14:00 | 20.1 | Mon | School Day | On | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 15:00 | 22 | Mon | School Day | On | Off | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 22.6 | Mon | School Day | On | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 21.4 | Mon | School Day | On | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 18:00 | 22.9 | Mon | School Day | On | Off | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.8 | Mon | School Day | Off | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 22.7 | Mon | School Day | Off | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.9 | Mon | School Day | Off | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 22:00 | 20.2 | Mon | School Day | Off | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 23:00 | 18.9 | Mon | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
Tue, 02/Aug | 24:00 | 17.4 | Tue | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 1:00 | 15.8 | Tue | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 2:00 | 14.5 | Tue | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 3:00 | 14.2 | Tue | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 4:00 | 12.6 | Tue | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 5:00 | 12.5 | Tue | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 6:00 | 12 | Tue | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 7:00 | 11.6 | Tue | School Day | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 8:00 | 12.5 | Tue | School Day | On | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 9:00 | 14.6 | Tue | School Day | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 10:00 | 17.3 | Tue | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 11:00 | 19.2 | Tue | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 12:00 | 19.8 | Tue | School Day | On | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 13:00 | 21 | Tue | School Day | On | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 14:00 | 22.3 | Tue | School Day | On | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 22.8 | Tue | School Day | On | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 24.1 | Tue | School Day | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23.7 | Tue | School Day | On | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 23.4 | Tue | School Day | On | Off | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.8 | Tue | School Day | Off | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 21.7 | Tue | School Day | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 21:00 | 21 | Tue | School Day | Off | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 22:00 | 20.3 | Tue | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 23:00 | 19.9 | Tue | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
Wed, 03/Aug | 24:00 | 19.4 | Wed | School Day | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 1:00 | 18.8 | Wed | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 2:00 | 17.5 | Wed | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 3:00 | 16.7 | Wed | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 4:00 | 15.7 | Wed | School Day | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 5:00 | 15.6 | Wed | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 6:00 | 14.5 | Wed | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 7:00 | 14.6 | Wed | School Day | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 8:00 | 15 | Wed | School Day | On | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 9:00 | 16.8 | Wed | School Day | On | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 10:00 | 19.1 | Wed | School Day | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 11:00 | 21.7 | Wed | School Day | On | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 12:00 | 22.7 | Wed | School Day | On | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 23.4 | Wed | School Day | On | Off | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 24.4 | Wed | School Day | On | Off | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 25.4 | Wed | School Day | On | Off | 22 | 22.34 | -0.34 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 25.9 | Wed | School Day | On | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.9 | Wed | School Day | On | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.2 | Wed | School Day | On | Off | 22 | 22.42 | -0.42 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 27.4 | Wed | School Day | Off | Off | 22 | 22.54 | -0.54 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 27 | Wed | School Day | Off | Off | 22 | 22.5 | -0.5 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 26.3 | Wed | School Day | Off | Off | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 24.4 | Wed | School Day | Off | Off | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 23 | Wed | School Day | Off | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Thu, 04/Aug | 24:00 | 21.2 | Thu | School Day | Off | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 1:00 | 19.6 | Thu | School Day | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 2:00 | 18.3 | Thu | School Day | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 3:00 | 16.6 | Thu | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 4:00 | 15.8 | Thu | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 5:00 | 14.6 | Thu | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 6:00 | 13.6 | Thu | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 7:00 | 13.1 | Thu | School Day | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 8:00 | 13.5 | Thu | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 9:00 | 15.1 | Thu | School Day | On | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 10:00 | 17.3 | Thu | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 11:00 | 18.7 | Thu | School Day | On | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 12:00 | 19.8 | Thu | School Day | On | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 13:00 | 21.6 | Thu | School Day | On | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 14:00 | 23 | Thu | School Day | On | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 24.5 | Thu | School Day | On | Off | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 25.9 | Thu | School Day | On | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26.1 | Thu | School Day | On | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.1 | Thu | School Day | On | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 26.3 | Thu | School Day | Off | Off | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25.5 | Thu | School Day | Off | Off | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24.9 | Thu | School Day | Off | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23.5 | Thu | School Day | Off | Off | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.7 | Thu | School Day | Off | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
Fri, 05/Aug | 24:00 | 20.3 | Fri | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 1:00 | 18.8 | Fri | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 2:00 | 17.5 | Fri | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 3:00 | 16.4 | Fri | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 4:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 5:00 | 14.4 | Fri | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 6:00 | 14 | Fri | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 7:00 | 13.6 | Fri | School Day | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 8:00 | 13.5 | Fri | School Day | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 9:00 | 15.2 | Fri | School Day | On | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 10:00 | 17.1 | Fri | School Day | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 11:00 | 19.4 | Fri | School Day | On | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 12:00 | 21.7 | Fri | School Day | On | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 13:00 | 23.2 | Fri | School Day | On | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 25.1 | Fri | School Day | On | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26 | Fri | School Day | On | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27.2 | Fri | School Day | On | Off | 22 | 22.52 | -0.52 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.5 | Fri | School Day | On | Off | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 28 | Fri | School Day | On | Off | 22 | 22.6 | -0.6 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 27.7 | Fri | School Day | Off | Off | 22 | 22.57 | -0.57 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 27.2 | Fri | School Day | Off | Off | 22 | 22.52 | -0.52 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 26.3 | Fri | School Day | Off | Off | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 24.1 | Fri | School Day | Off | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 22.4 | Fri | School Day | Off | Off | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Sat, 06/Aug | 24:00 | 20.7 | Sat | WE | Off | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 1:00 | 20.4 | Sat | WE | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 2:00 | 19.8 | Sat | WE | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 3:00 | 18.7 | Sat | WE | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 4:00 | 16.6 | Sat | WE | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 5:00 | 15.7 | Sat | WE | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 6:00 | 16.6 | Sat | WE | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 7:00 | 16.1 | Sat | WE | On | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 8:00 | 16.6 | Sat | WE | On | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 9:00 | 18.1 | Sat | WE | On | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 10:00 | 20.8 | Sat | WE | On | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 11:00 | 23.2 | Sat | WE | On | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 25.2 | Sat | WE | On | Off | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 26.5 | Sat | WE | On | Off | 22 | 22.45 | -0.45 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 27.8 | Sat | WE | On | Off | 22 | 22.58 | -0.58 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 28.3 | Sat | WE | On | Off | 22 | 22.63 | -0.63 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 29.4 | Sat | WE | On | Off | 22 | 22.74 | -0.74 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 30.3 | Sat | WE | On | Off | 22 | 22.83 | -0.83 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 29.2 | Sat | WE | On | Off | 22 | 22.72 | -0.72 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 29.3 | Sat | WE | Off | Off | 22 | 22.73 | -0.73 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 28.2 | Sat | WE | Off | Off | 22 | 22.62 | -0.62 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 26.8 | Sat | WE | Off | Off | 22 | 22.48 | -0.48 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 25.8 | Sat | WE | Off | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 24.1 | Sat | WE | Off | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Sun, 07/Aug | 24:00 | 22.8 | Sun | WE | Off | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 1:00 | 21.5 | Sun | WE | Off | Off | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 2:00 | 20.2 | Sun | WE | Off | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 3:00 | 19.1 | Sun | WE | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 4:00 | 17.9 | Sun | WE | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 5:00 | 16.6 | Sun | WE | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 6:00 | 17 | Sun | WE | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 7:00 | 16.1 | Sun | WE | On | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 8:00 | 16.7 | Sun | WE | On | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 9:00 | 18 | Sun | WE | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 10:00 | 19.6 | Sun | WE | On | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 11:00 | 21.4 | Sun | WE | On | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 12:00 | 23.2 | Sun | WE | On | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 24 | Sun | WE | On | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 25.7 | Sun | WE | On | Off | 22 | 22.37 | -0.37 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26.8 | Sun | WE | On | Off | 22 | 22.48 | -0.48 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 28.2 | Sun | WE | On | Off | 22 | 22.62 | -0.62 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.5 | Sun | WE | On | Off | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 27.3 | Sun | WE | On | Off | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 27 | Sun | WE | Off | Off | 22 | 22.5 | -0.5 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 26.4 | Sun | WE | Off | Off | 22 | 22.44 | -0.44 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24.9 | Sun | WE | Off | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23.2 | Sun | WE | Off | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 22.7 | Sun | WE | Off | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Mon, 08/Aug | 24:00 | 20.3 | Mon | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 1:00 | 19.6 | Mon | School Day | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 2:00 | 19.8 | Mon | School Day | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 3:00 | 19.1 | Mon | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 4:00 | 18.4 | Mon | School Day | Off | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 5:00 | 17.5 | Mon | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 6:00 | 16.7 | Mon | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 7:00 | 16.4 | Mon | School Day | On | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 8:00 | 16.5 | Mon | School Day | On | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 9:00 | 18.5 | Mon | School Day | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 10:00 | 20.3 | Mon | School Day | On | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 11:00 | 21.5 | Mon | School Day | On | Off | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 12:00 | 21.7 | Mon | School Day | On | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 13:00 | 23.7 | Mon | School Day | On | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 25.1 | Mon | School Day | On | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27.2 | Mon | School Day | On | Off | 22 | 22.52 | -0.52 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26.1 | Mon | School Day | On | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.1 | Mon | School Day | On | Off | 22 | 22.51 | -0.51 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.2 | Mon | School Day | On | Off | 22 | 22.42 | -0.42 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.9 | Mon | School Day | Off | Off | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25.4 | Mon | School Day | Off | Off | 22 | 22.34 | -0.34 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24.7 | Mon | School Day | Off | Off | 22 | 22.27 | -0.27 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 24 | Mon | School Day | Off | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 22.2 | Mon | School Day | Off | Off | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Tue, 09/Aug | 24:00 | 21.4 | Tue | School Day | Off | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 1:00 | 19.3 | Tue | School Day | Off | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 2:00 | 18.9 | Tue | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 3:00 | 18.8 | Tue | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 4:00 | 18.1 | Tue | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 5:00 | 17.5 | Tue | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 6:00 | 17.7 | Tue | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 7:00 | 17.3 | Tue | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 8:00 | 17.3 | Tue | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 9:00 | 18.9 | Tue | School Day | On | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 10:00 | 20.9 | Tue | School Day | On | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 11:00 | 23.1 | Tue | School Day | On | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 12:00 | 26 | Tue | School Day | On | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 26 | Tue | School Day | On | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 26.4 | Tue | School Day | On | Off | 22 | 22.44 | -0.44 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 25.8 | Tue | School Day | On | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26.8 | Tue | School Day | On | Off | 22 | 22.48 | -0.48 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26.1 | Tue | School Day | On | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.6 | Tue | School Day | On | Off | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 24.8 | Tue | School Day | Off | Off | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 23.6 | Tue | School Day | Off | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 22.8 | Tue | School Day | Off | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22 | Tue | School Day | Off | Off | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.3 | Tue | School Day | Off | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
Wed, 10/Aug | 24:00 | 20.6 | Wed | School Day | Off | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 1:00 | 20.1 | Wed | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 2:00 | 19.9 | Wed | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 3:00 | 19.6 | Wed | School Day | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 4:00 | 19.2 | Wed | School Day | Off | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 5:00 | 18.9 | Wed | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 6:00 | 19 | Wed | School Day | Off | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 7:00 | 19 | Wed | School Day | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 8:00 | 18.9 | Wed | School Day | On | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 9:00 | 19 | Wed | School Day | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 10:00 | 17.6 | Wed | School Day | On | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 11:00 | 17.7 | Wed | School Day | On | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 12:00 | 17.6 | Wed | School Day | On | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 13:00 | 17.6 | Wed | School Day | On | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 14:00 | 16.7 | Wed | School Day | On | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 15:00 | 17.7 | Wed | School Day | On | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 16:00 | 18.8 | Wed | School Day | On | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 17:00 | 20.1 | Wed | School Day | On | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 18:00 | 20.8 | Wed | School Day | On | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 19:00 | 21.2 | Wed | School Day | Off | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 20:00 | 21.6 | Wed | School Day | Off | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 21:00 | 20.8 | Wed | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 22:00 | 20.1 | Wed | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 23:00 | 19.2 | Wed | School Day | Off | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
Thu, 11/Aug | 24:00 | 17.1 | Thu | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 1:00 | 16.7 | Thu | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 2:00 | 16.6 | Thu | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 3:00 | 16.4 | Thu | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 4:00 | 16.2 | Thu | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 5:00 | 16.1 | Thu | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 6:00 | 16.1 | Thu | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 7:00 | 16.3 | Thu | School Day | On | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 8:00 | 16.5 | Thu | School Day | On | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 9:00 | 17.1 | Thu | School Day | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 10:00 | 17.1 | Thu | School Day | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 11:00 | 17.9 | Thu | School Day | On | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 12:00 | 19.2 | Thu | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 13:00 | 21.3 | Thu | School Day | On | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 14:00 | 23.1 | Thu | School Day | On | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 24 | Thu | School Day | On | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 24.9 | Thu | School Day | On | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 24.9 | Thu | School Day | On | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 24.8 | Thu | School Day | On | Off | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 23.8 | Thu | School Day | Off | Off | 22 | 22.18 | -0.18 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 22.6 | Thu | School Day | Off | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.6 | Thu | School Day | Off | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 22:00 | 20.4 | Thu | School Day | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 23:00 | 19.9 | Thu | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
Fri, 12/Aug | 24:00 | 19.1 | Fri | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 1:00 | 18.6 | Fri | School Day | Off | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 2:00 | 18.1 | Fri | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 3:00 | 17.8 | Fri | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 4:00 | 17.6 | Fri | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 5:00 | 17.3 | Fri | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 6:00 | 16 | Fri | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 7:00 | 17 | Fri | School Day | On | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 8:00 | 17.2 | Fri | School Day | On | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 9:00 | 17.8 | Fri | School Day | On | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 10:00 | 19 | Fri | School Day | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 11:00 | 20 | Fri | School Day | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 12:00 | 21.9 | Fri | School Day | On | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 13:00 | 23.4 | Fri | School Day | On | Off | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 22.6 | Fri | School Day | On | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.1 | Fri | School Day | On | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23.6 | Fri | School Day | On | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.4 | Fri | School Day | On | Off | 22 | 22.34 | -0.34 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 23.8 | Fri | School Day | On | Off | 22 | 22.18 | -0.18 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 23.9 | Fri | School Day | Off | Off | 22 | 22.19 | -0.19 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 22.8 | Fri | School Day | Off | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21 | Fri | School Day | Off | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 22:00 | 19.3 | Fri | School Day | Off | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 23:00 | 17.5 | Fri | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
Sat, 13/Aug | 24:00 | 16 | Sat | WE | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 1:00 | 16.1 | Sat | WE | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 2:00 | 16.1 | Sat | WE | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 3:00 | 14.3 | Sat | WE | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 4:00 | 15.1 | Sat | WE | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 5:00 | 14.9 | Sat | WE | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 6:00 | 14.5 | Sat | WE | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 7:00 | 14.6 | Sat | WE | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 8:00 | 15 | Sat | WE | On | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 9:00 | 16.4 | Sat | WE | On | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 10:00 | 18.7 | Sat | WE | On | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 11:00 | 20.7 | Sat | WE | On | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 12:00 | 21.1 | Sat | WE | On | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 13:00 | 20.2 | Sat | WE | On | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 14:00 | 21.1 | Sat | WE | On | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 15:00 | 20.9 | Sat | WE | On | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 16:00 | 21.7 | Sat | WE | On | Off | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 17:00 | 22.9 | Sat | WE | On | Off | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.5 | Sat | WE | On | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 21.4 | Sat | WE | Off | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 20:00 | 21.4 | Sat | WE | Off | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 21:00 | 20.9 | Sat | WE | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 22:00 | 20.3 | Sat | WE | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 23:00 | 19.6 | Sat | WE | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
Sun, 14/Aug | 24:00 | 19.6 | Sun | WE | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 1:00 | 19.6 | Sun | WE | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 2:00 | 18.3 | Sun | WE | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 3:00 | 18.2 | Sun | WE | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 4:00 | 17.8 | Sun | WE | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 5:00 | 17.3 | Sun | WE | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 6:00 | 16.1 | Sun | WE | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 7:00 | 16.1 | Sun | WE | On | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 8:00 | 16.5 | Sun | WE | On | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 9:00 | 17.3 | Sun | WE | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 10:00 | 19.1 | Sun | WE | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 11:00 | 20.5 | Sun | WE | On | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 12:00 | 21.8 | Sun | WE | On | Off | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0
| 13:00 | 23 | Sun | WE | On | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 24.9 | Sun | WE | On | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 25 | Sun | WE | On | Off | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 21.5 | Sun | WE | On | Off | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 17:00 | 22.8 | Sun | WE | On | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 23.3 | Sun | WE | On | Off | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.8 | Sun | WE | Off | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 23.2 | Sun | WE | Off | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.3 | Sun | WE | Off | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 22:00 | 20.4 | Sun | WE | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 23:00 | 20.6 | Sun | WE | Off | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
Mon, 15/Aug | 24:00 | 20.3 | Mon | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 1:00 | 20.5 | Mon | School Day | Off | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 2:00 | 20.6 | Mon | School Day | Off | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 3:00 | 21.1 | Mon | School Day | Off | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 4:00 | 20.6 | Mon | School Day | Off | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 5:00 | 20.1 | Mon | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 6:00 | 17.6 | Mon | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 7:00 | 17.5 | Mon | School Day | On | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 8:00 | 17.6 | Mon | School Day | On | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 9:00 | 18.1 | Mon | School Day | On | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 10:00 | 19.2 | Mon | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 11:00 | 21 | Mon | School Day | On | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 12:00 | 22.5 | Mon | School Day | On | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 23.3 | Mon | School Day | On | Off | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 24.3 | Mon | School Day | On | Off | 22 | 22.23 | -0.23 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 24.4 | Mon | School Day | On | Off | 22 | 22.24 | -0.24 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 24.1 | Mon | School Day | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25 | Mon | School Day | On | Off | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 23.8 | Mon | School Day | On | Off | 22 | 22.18 | -0.18 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 23.7 | Mon | School Day | Off | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 22.3 | Mon | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.1 | Mon | School Day | Off | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 22:00 | 20 | Mon | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 23:00 | 19.5 | Mon | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
Tue, 16/Aug | 24:00 | 19.2 | Tue | School Day | Off | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 1:00 | 19.1 | Tue | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 2:00 | 18.8 | Tue | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 3:00 | 18.3 | Tue | School Day | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 4:00 | 18.1 | Tue | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 5:00 | 18.4 | Tue | School Day | Off | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 6:00 | 18.4 | Tue | School Day | Off | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 7:00 | 18 | Tue | School Day | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 8:00 | 18.1 | Tue | School Day | On | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 9:00 | 18.6 | Tue | School Day | On | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 10:00 | 19.2 | Tue | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 11:00 | 20.3 | Tue | School Day | On | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 12:00 | 22.1 | Tue | School Day | On | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 22.5 | Tue | School Day | On | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 23.3 | Tue | School Day | On | Off | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 22.7 | Tue | School Day | On | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 25.2 | Tue | School Day | On | Off | 22 | 22.32 | -0.32 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23.7 | Tue | School Day | On | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 23.6 | Tue | School Day | On | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.7 | Tue | School Day | Off | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 22.7 | Tue | School Day | Off | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.2 | Tue | School Day | Off | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 22:00 | 20.3 | Tue | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 23:00 | 19.4 | Tue | School Day | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
Wed, 17/Aug | 24:00 | 16.7 | Wed | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 1:00 | 16.5 | Wed | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 2:00 | 16.7 | Wed | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 3:00 | 16.1 | Wed | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 4:00 | 15.5 | Wed | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 5:00 | 14.9 | Wed | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 6:00 | 14.3 | Wed | School Day | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 7:00 | 14.1 | Wed | School Day | On | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 8:00 | 14.6 | Wed | School Day | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 9:00 | 16 | Wed | School Day | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 10:00 | 17.9 | Wed | School Day | On | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 11:00 | 20 | Wed | School Day | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 12:00 | 21 | Wed | School Day | On | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 13:00 | 22.2 | Wed | School Day | On | Off | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 23.3 | Wed | School Day | On | Off | 22 | 22.13 | -0.13 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 22.5 | Wed | School Day | On | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 19.6 | Wed | School Day | On | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 17:00 | 21.2 | Wed | School Day | On | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 18:00 | 22.5 | Wed | School Day | On | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 20.9 | Wed | School Day | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 20:00 | 19.8 | Wed | School Day | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 21:00 | 18.9 | Wed | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 22:00 | 17.9 | Wed | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 23:00 | 16.9 | Wed | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
Thu, 18/Aug | 24:00 | 14.9 | Thu | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 1:00 | 14.4 | Thu | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 2:00 | 14.1 | Thu | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 3:00 | 13.6 | Thu | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 4:00 | 11.7 | Thu | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 5:00 | 11.4 | Thu | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 6:00 | 11.5 | Thu | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 7:00 | 11.9 | Thu | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 8:00 | 12.3 | Thu | School Day | On | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 9:00 | 13.4 | Thu | School Day | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 10:00 | 15.8 | Thu | School Day | On | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 11:00 | 18.5 | Thu | School Day | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 12:00 | 20 | Thu | School Day | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 13:00 | 21.8 | Thu | School Day | On | Off | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0
| 14:00 | 22.1 | Thu | School Day | On | Off | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 22.2 | Thu | School Day | On | Off | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23.5 | Thu | School Day | On | Off | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 24 | Thu | School Day | On | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.7 | Thu | School Day | On | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 23 | Thu | School Day | Off | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 22.3 | Thu | School Day | Off | Off | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.3 | Thu | School Day | Off | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 22:00 | 19.7 | Thu | School Day | Off | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 23:00 | 17.8 | Thu | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
Fri, 19/Aug | 24:00 | 16.9 | Fri | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 1:00 | 15.5 | Fri | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 2:00 | 14.5 | Fri | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 3:00 | 13.9 | Fri | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 4:00 | 12.3 | Fri | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 5:00 | 12.5 | Fri | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 6:00 | 12.5 | Fri | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 7:00 | 13.1 | Fri | School Day | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 8:00 | 14 | Fri | School Day | On | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 9:00 | 15.1 | Fri | School Day | On | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 10:00 | 17.2 | Fri | School Day | On | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 11:00 | 19.5 | Fri | School Day | On | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 12:00 | 21.5 | Fri | School Day | On | Off | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 13:00 | 23.7 | Fri | School Day | On | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 26.1 | Fri | School Day | On | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27.2 | Fri | School Day | On | Off | 22 | 22.52 | -0.52 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27.3 | Fri | School Day | On | Off | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 28 | Fri | School Day | On | Off | 22 | 22.6 | -0.6 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 27.2 | Fri | School Day | On | Off | 22 | 22.52 | -0.52 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 27 | Fri | School Day | Off | Off | 22 | 22.5 | -0.5 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 26.1 | Fri | School Day | Off | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 25 | Fri | School Day | Off | Off | 22 | 22.3 | -0.3 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 24 | Fri | School Day | Off | Off | 22 | 22.2 | -0.2 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 22.7 | Fri | School Day | Off | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
Sat, 20/Aug | 24:00 | 21.3 | Sat | WE | Off | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 1:00 | 20 | Sat | WE | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 2:00 | 18.5 | Sat | WE | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 3:00 | 17.3 | Sat | WE | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 4:00 | 17.1 | Sat | WE | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 5:00 | 16.5 | Sat | WE | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 6:00 | 15.2 | Sat | WE | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 7:00 | 14.6 | Sat | WE | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 8:00 | 15.1 | Sat | WE | On | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 9:00 | 17.1 | Sat | WE | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 10:00 | 20.2 | Sat | WE | On | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 11:00 | 21.9 | Sat | WE | On | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 12:00 | 24.1 | Sat | WE | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 26.3 | Sat | WE | On | Off | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 28.1 | Sat | WE | On | Off | 22 | 22.61 | -0.61 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 29.4 | Sat | WE | On | Off | 22 | 22.74 | -0.74 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 29.6 | Sat | WE | On | Off | 22 | 22.76 | -0.76 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 28.7 | Sat | WE | On | Off | 22 | 22.67 | -0.67 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 28 | Sat | WE | On | Off | 22 | 22.6 | -0.6 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 26.9 | Sat | WE | Off | Off | 22 | 22.49 | -0.49 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25.5 | Sat | WE | Off | Off | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 24.1 | Sat | WE | Off | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.2 | Sat | WE | Off | Off | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 20.9 | Sat | WE | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
Sun, 21/Aug | 24:00 | 20 | Sun | WE | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 1:00 | 19.7 | Sun | WE | Off | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 2:00 | 20.1 | Sun | WE | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 3:00 | 20.1 | Sun | WE | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 4:00 | 20.8 | Sun | WE | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 5:00 | 19.9 | Sun | WE | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 6:00 | 18.9 | Sun | WE | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 7:00 | 17.9 | Sun | WE | On | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 8:00 | 17.1 | Sun | WE | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 9:00 | 17.5 | Sun | WE | On | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 10:00 | 19.1 | Sun | WE | On | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 11:00 | 20.6 | Sun | WE | On | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 12:00 | 21.4 | Sun | WE | On | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 13:00 | 22.6 | Sun | WE | On | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 24.1 | Sun | WE | On | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 25.4 | Sun | WE | On | Off | 22 | 22.34 | -0.34 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26.3 | Sun | WE | On | Off | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26.9 | Sun | WE | On | Off | 22 | 22.49 | -0.49 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 27 | Sun | WE | On | Off | 22 | 22.5 | -0.5 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 26.6 | Sun | WE | Off | Off | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25.8 | Sun | WE | Off | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.9 | Sun | WE | Off | Off | 22 | 22.19 | -0.19 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 21.9 | Sun | WE | Off | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 23:00 | 20.1 | Sun | WE | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
Mon, 22/Aug | 24:00 | 19.2 | Mon | School Day | Off | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 1:00 | 16.8 | Mon | School Day | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 2:00 | 15 | Mon | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 3:00 | 14.1 | Mon | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 4:00 | 14.7 | Mon | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 5:00 | 13.1 | Mon | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 6:00 | 12.7 | Mon | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 7:00 | 13.1 | Mon | School Day | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 8:00 | 13.6 | Mon | School Day | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 9:00 | 15.1 | Mon | School Day | On | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 10:00 | 16.6 | Mon | School Day | On | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 11:00 | 19.4 | Mon | School Day | On | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 12:00 | 21.3 | Mon | School Day | On | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 13:00 | 22 | Mon | School Day | On | Off | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 22 | Mon | School Day | On | Off | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23 | Mon | School Day | On | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23.4 | Mon | School Day | On | Off | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23.7 | Mon | School Day | On | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 25.6 | Mon | School Day | On | Off | 22 | 22.36 | -0.36 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 24.2 | Mon | School Day | Off | Off | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.2 | Mon | School Day | Off | Off | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.2 | Mon | School Day | Off | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 20.7 | Mon | School Day | Off | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 23:00 | 20.5 | Mon | School Day | Off | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
Tue, 23/Aug | 24:00 | 19.2 | Tue | School Day | Off | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 1:00 | 18.2 | Tue | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 2:00 | 17 | Tue | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 3:00 | 16.3 | Tue | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 4:00 | 15.1 | Tue | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 5:00 | 13.2 | Tue | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 6:00 | 12.5 | Tue | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 7:00 | 11.3 | Tue | School Day | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 8:00 | 11.5 | Tue | School Day | On | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 9:00 | 12.7 | Tue | School Day | On | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 10:00 | 15.4 | Tue | School Day | On | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 11:00 | 18.1 | Tue | School Day | On | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 12:00 | 20.2 | Tue | School Day | On | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 13:00 | 21 | Tue | School Day | On | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 14:00 | 22.8 | Tue | School Day | On | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 24.3 | Tue | School Day | On | Off | 22 | 22.23 | -0.23 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 25.3 | Tue | School Day | On | Off | 22 | 22.33 | -0.33 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 25.8 | Tue | School Day | On | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26 | Tue | School Day | On | Off | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.8 | Tue | School Day | Off | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.1 | Tue | School Day | Off | Off | 22 | 22.21 | -0.21 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.6 | Tue | School Day | Off | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 22:00 | 20.4 | Tue | School Day | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 23:00 | 19.6 | Tue | School Day | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
Wed, 24/Aug | 24:00 | 18.3 | Wed | School Day | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 1:00 | 17.2 | Wed | School Day | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 2:00 | 15.1 | Wed | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 3:00 | 15.5 | Wed | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 4:00 | 13.5 | Wed | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 5:00 | 13.4 | Wed | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 6:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 7:00 | 12.7 | Wed | School Day | On | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 8:00 | 13.2 | Wed | School Day | On | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 9:00 | 14.5 | Wed | School Day | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 10:00 | 16.7 | Wed | School Day | On | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 11:00 | 19.2 | Wed | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 12:00 | 21 | Wed | School Day | On | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 13:00 | 23.4 | Wed | School Day | On | Off | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 24.9 | Wed | School Day | On | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 25.8 | Wed | School Day | On | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27.1 | Wed | School Day | On | Off | 22 | 22.51 | -0.51 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.3 | Wed | School Day | On | Off | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.2 | Wed | School Day | On | Off | 22 | 22.42 | -0.42 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 24.8 | Wed | School Day | Off | Off | 22 | 22.28 | -0.28 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 23.7 | Wed | School Day | Off | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.9 | Wed | School Day | Off | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 22:00 | 20.2 | Wed | School Day | Off | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 23:00 | 18.9 | Wed | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
Thu, 25/Aug | 24:00 | 17.6 | Thu | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 1:00 | 17.5 | Thu | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 2:00 | 17.8 | Thu | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 3:00 | 17.8 | Thu | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 4:00 | 17.5 | Thu | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 5:00 | 17.1 | Thu | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 6:00 | 17.6 | Thu | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 7:00 | 17.6 | Thu | School Day | On | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 8:00 | 17.6 | Thu | School Day | On | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 9:00 | 17.9 | Thu | School Day | On | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 10:00 | 19.3 | Thu | School Day | On | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 11:00 | 20.5 | Thu | School Day | On | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 12:00 | 21.3 | Thu | School Day | On | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 13:00 | 22.8 | Thu | School Day | On | Off | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 21.9 | Thu | School Day | On | Off | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 15:00 | 21.5 | Thu | School Day | On | Off | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 16:00 | 21 | Thu | School Day | On | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 17:00 | 18.5 | Thu | School Day | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 18:00 | 17.8 | Thu | School Day | On | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 19:00 | 17.9 | Thu | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 20:00 | 17.6 | Thu | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 21:00 | 16.2 | Thu | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 22:00 | 16.7 | Thu | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 23:00 | 16.7 | Thu | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
Fri, 26/Aug | 24:00 | 16 | Fri | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 1:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 2:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 3:00 | 15.5 | Fri | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 4:00 | 15.7 | Fri | School Day | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 5:00 | 15.5 | Fri | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 6:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 7:00 | 15.7 | Fri | School Day | On | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 8:00 | 15.7 | Fri | School Day | On | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 9:00 | 16.2 | Fri | School Day | On | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 10:00 | 16.7 | Fri | School Day | On | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 11:00 | 17.4 | Fri | School Day | On | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 12:00 | 18.5 | Fri | School Day | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 13:00 | 20.2 | Fri | School Day | On | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 14:00 | 22.6 | Fri | School Day | On | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.7 | Fri | School Day | On | Off | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 21.8 | Fri | School Day | On | Off | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0
| 17:00 | 19.2 | Fri | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 18:00 | 19.9 | Fri | School Day | On | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 19:00 | 20.9 | Fri | School Day | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 20:00 | 18.6 | Fri | School Day | Off | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 21:00 | 18 | Fri | School Day | Off | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 22:00 | 17.9 | Fri | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 23:00 | 17.7 | Fri | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
Sat, 27/Aug | 24:00 | 17.4 | Sat | WE | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 1:00 | 17.1 | Sat | WE | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 2:00 | 17 | Sat | WE | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 3:00 | 16.9 | Sat | WE | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 4:00 | 16.8 | Sat | WE | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 5:00 | 16.2 | Sat | WE | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 6:00 | 15.6 | Sat | WE | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 7:00 | 14.9 | Sat | WE | On | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 8:00 | 14.8 | Sat | WE | On | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 9:00 | 14.5 | Sat | WE | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 10:00 | 15.1 | Sat | WE | On | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 11:00 | 15.9 | Sat | WE | On | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 12:00 | 16.8 | Sat | WE | On | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 13:00 | 18.6 | Sat | WE | On | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 14:00 | 18.6 | Sat | WE | On | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 15:00 | 18.8 | Sat | WE | On | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 16:00 | 20 | Sat | WE | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 17:00 | 19.3 | Sat | WE | On | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 18:00 | 19.9 | Sat | WE | On | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 19:00 | 18.3 | Sat | WE | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 20:00 | 18.3 | Sat | WE | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 21:00 | 17.1 | Sat | WE | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 22:00 | 16.2 | Sat | WE | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 23:00 | 15.3 | Sat | WE | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
Sun, 28/Aug | 24:00 | 14 | Sun | WE | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 1:00 | 14.1 | Sun | WE | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 2:00 | 12.7 | Sun | WE | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 3:00 | 12.2 | Sun | WE | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 4:00 | 11.9 | Sun | WE | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 5:00 | 11.5 | Sun | WE | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 6:00 | 10.7 | Sun | WE | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 7:00 | 10.7 | Sun | WE | On | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 8:00 | 10.2 | Sun | WE | On | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 9:00 | 11.2 | Sun | WE | On | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 10:00 | 13 | Sun | WE | On | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 11:00 | 14.3 | Sun | WE | On | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 12:00 | 16.2 | Sun | WE | On | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 13:00 | 17.8 | Sun | WE | On | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 14:00 | 18.9 | Sun | WE | On | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 15:00 | 19.8 | Sun | WE | On | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 16:00 | 19.3 | Sun | WE | On | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 17:00 | 20.9 | Sun | WE | On | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 18:00 | 20.9 | Sun | WE | On | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 19:00 | 20.3 | Sun | WE | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 20:00 | 19.9 | Sun | WE | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 21:00 | 19.1 | Sun | WE | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 22:00 | 17.2 | Sun | WE | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 23:00 | 16.2 | Sun | WE | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
Mon, 29/Aug | 24:00 | 15.7 | Mon | School Day | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 1:00 | 14.2 | Mon | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 2:00 | 12.7 | Mon | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 3:00 | 12.3 | Mon | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 4:00 | 12.1 | Mon | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 5:00 | 11.6 | Mon | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 6:00 | 12.5 | Mon | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 7:00 | 13 | Mon | School Day | On | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 8:00 | 13.2 | Mon | School Day | On | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 9:00 | 14.4 | Mon | School Day | On | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 10:00 | 15.5 | Mon | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 11:00 | 16.2 | Mon | School Day | On | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 12:00 | 17.4 | Mon | School Day | On | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 13:00 | 17.6 | Mon | School Day | On | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 14:00 | 18.5 | Mon | School Day | On | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 15:00 | 19.7 | Mon | School Day | On | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 16:00 | 20.9 | Mon | School Day | On | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 17:00 | 20.5 | Mon | School Day | On | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 18:00 | 20.3 | Mon | School Day | On | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 19:00 | 20.1 | Mon | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 20:00 | 20.1 | Mon | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 21:00 | 20.1 | Mon | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 22:00 | 20 | Mon | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 23:00 | 19.4 | Mon | School Day | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
Tue, 30/Aug | 24:00 | 19.2 | Tue | School Day | Off | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 1:00 | 18.5 | Tue | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 2:00 | 18.2 | Tue | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 3:00 | 17.5 | Tue | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 4:00 | 17.4 | Tue | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 5:00 | 17.3 | Tue | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 6:00 | 17.5 | Tue | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 7:00 | 17.5 | Tue | School Day | On | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 8:00 | 18 | Tue | School Day | On | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 9:00 | 18.1 | Tue | School Day | On | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 10:00 | 19.3 | Tue | School Day | On | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 11:00 | 20 | Tue | School Day | On | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 12:00 | 20.5 | Tue | School Day | On | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 13:00 | 21.3 | Tue | School Day | On | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 14:00 | 22.6 | Tue | School Day | On | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 25.8 | Tue | School Day | On | Off | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26.5 | Tue | School Day | On | Off | 22 | 22.45 | -0.45 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26.9 | Tue | School Day | On | Off | 22 | 22.49 | -0.49 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.1 | Tue | School Day | On | Off | 22 | 22.41 | -0.41 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 24.9 | Tue | School Day | Off | Off | 22 | 22.29 | -0.29 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 23 | Tue | School Day | Off | Off | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21 | Tue | School Day | Off | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 22:00 | 19.7 | Tue | School Day | Off | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 23:00 | 18.7 | Tue | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
Wed, 31/Aug | 24:00 | 18.4 | Wed | School Day | Off | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 1:00 | 18.2 | Wed | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 2:00 | 18.2 | Wed | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 3:00 | 17.8 | Wed | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 4:00 | 16.3 | Wed | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 5:00 | 14.7 | Wed | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 6:00 | 13.7 | Wed | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 7:00 | 13.6 | Wed | School Day | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 8:00 | 13.2 | Wed | School Day | On | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 9:00 | 14.2 | Wed | School Day | On | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 10:00 | 15.9 | Wed | School Day | On | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 11:00 | 16.7 | Wed | School Day | On | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 12:00 | 17.9 | Wed | School Day | On | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 13:00 | 19.2 | Wed | School Day | On | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 14:00 | 19.6 | Wed | School Day | On | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 15:00 | 20.2 | Wed | School Day | On | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 16:00 | 21.2 | Wed | School Day | On | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 17:00 | 20.4 | Wed | School Day | On | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 18:00 | 20.8 | Wed | School Day | On | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 19:00 | 20.8 | Wed | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 20:00 | 20 | Wed | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 21:00 | 18.9 | Wed | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 22:00 | 17.8 | Wed | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 23:00 | 17.1 | Wed | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
Thu, 01/Sep | 24:00 | 16.7 | Thu | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 1:00 | 14.6 | Thu | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 2:00 | 13.6 | Thu | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 3:00 | 14 | Thu | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 4:00 | 13.6 | Thu | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 5:00 | 12.1 | Thu | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 6:00 | 11.2 | Thu | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 7:00 | 10.9 | Thu | School Day | On | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 8:00 | 10.7 | Thu | School Day | On | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 9:00 | 11.9 | Thu | School Day | On | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 10:00 | 14.2 | Thu | School Day | On | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 11:00 | 17.1 | Thu | School Day | On | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 12:00 | 18.7 | Thu | School Day | On | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 13:00 | 19.8 | Thu | School Day | On | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 14:00 | 20.8 | Thu | School Day | On | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 15:00 | 20.4 | Thu | School Day | On | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 16:00 | 20.1 | Thu | School Day | On | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 17:00 | 21.1 | Thu | School Day | On | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 18:00 | 21.2 | Thu | School Day | On | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 19:00 | 20.8 | Thu | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 20:00 | 20.8 | Thu | School Day | Off | Off | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 21:00 | 19.4 | Thu | School Day | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 22:00 | 18.7 | Thu | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 23:00 | 16.9 | Thu | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
Fri, 02/Sep | 24:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 1:00 | 14.9 | Fri | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 2:00 | 14.1 | Fri | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 3:00 | 13.5 | Fri | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 4:00 | 13.2 | Fri | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 5:00 | 12.4 | Fri | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 6:00 | 12.9 | Fri | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 7:00 | 13.3 | Fri | School Day | On | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 8:00 | 12.5 | Fri | School Day | On | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 9:00 | 13.4 | Fri | School Day | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 10:00 | 14.3 | Fri | School Day | On | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 11:00 | 16 | Fri | School Day | On | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 12:00 | 17.3 | Fri | School Day | On | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 13:00 | 17 | Fri | School Day | On | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 14:00 | 17.4 | Fri | School Day | On | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 15:00 | 17.8 | Fri | School Day | On | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 16:00 | 18.2 | Fri | School Day | On | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 17:00 | 18.8 | Fri | School Day | On | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 18:00 | 18.9 | Fri | School Day | On | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 19:00 | 17.8 | Fri | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 20:00 | 18 | Fri | School Day | Off | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 21:00 | 16.8 | Fri | School Day | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 22:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 23:00 | 14.4 | Fri | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
Sat, 03/Sep | 24:00 | 14.5 | Sat | WE | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 1:00 | 13.6 | Sat | WE | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 2:00 | 13.3 | Sat | WE | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 3:00 | 11.9 | Sat | WE | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 4:00 | 10.9 | Sat | WE | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 5:00 | 9.9 | Sat | WE | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 6:00 | 9.8 | Sat | WE | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 7:00 | 9.5 | Sat | WE | On | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 8:00 | 9.1 | Sat | WE | On | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 9:00 | 10 | Sat | WE | On | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 10:00 | 12.2 | Sat | WE | On | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 11:00 | 14.7 | Sat | WE | On | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 12:00 | 15.5 | Sat | WE | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 13:00 | 16.5 | Sat | WE | On | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 14:00 | 17.4 | Sat | WE | On | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 15:00 | 18.6 | Sat | WE | On | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 16:00 | 19 | Sat | WE | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 17:00 | 19 | Sat | WE | On | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 18:00 | 19.5 | Sat | WE | On | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 19:00 | 18.4 | Sat | WE | Off | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 20:00 | 17.6 | Sat | WE | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 21:00 | 17.4 | Sat | WE | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 22:00 | 17 | Sat | WE | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 23:00 | 17 | Sat | WE | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
Sun, 04/Sep | 24:00 | 16 | Sun | WE | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 1:00 | 15.3 | Sun | WE | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 2:00 | 15.3 | Sun | WE | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 3:00 | 14.5 | Sun | WE | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 4:00 | 14.3 | Sun | WE | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 5:00 | 13.9 | Sun | WE | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 6:00 | 13.5 | Sun | WE | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 7:00 | 13.5 | Sun | WE | On | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 8:00 | 13.3 | Sun | WE | On | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 9:00 | 14.3 | Sun | WE | On | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 10:00 | 15.2 | Sun | WE | On | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 11:00 | 16.7 | Sun | WE | On | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 12:00 | 18.7 | Sun | WE | On | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 13:00 | 20.4 | Sun | WE | On | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 14:00 | 20.1 | Sun | WE | On | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 15:00 | 21.2 | Sun | WE | On | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 16:00 | 21.1 | Sun | WE | On | Off | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0
| 17:00 | 21.2 | Sun | WE | On | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 18:00 | 21.6 | Sun | WE | On | Off | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 19:00 | 20.9 | Sun | WE | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 20:00 | 20.4 | Sun | WE | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 21:00 | 19.8 | Sun | WE | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 22:00 | 19.4 | Sun | WE | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 23:00 | 17.3 | Sun | WE | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
Mon, 05/Sep | 24:00 | 15 | Mon | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 1:00 | 15 | Mon | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 2:00 | 13.9 | Mon | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 3:00 | 15.5 | Mon | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 4:00 | 15.6 | Mon | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 5:00 | 15.9 | Mon | School Day | Off | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 6:00 | 15.2 | Mon | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 7:00 | 15.3 | Mon | School Day | On | On | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 1.8509
| 8:00 | 15.3 | Mon | School Day | On | On | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 1.8509
| 9:00 | 16 | Mon | School Day | On | On | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 1.6575
| 10:00 | 16.5 | Mon | School Day | On | On | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 1.5194
| 11:00 | 17.8 | Mon | School Day | On | On | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 1.1602
| 12:00 | 19.7 | Mon | School Day | On | On | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0.63537
| 13:00 | 20.8 | Mon | School Day | On | On | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0.3315
| 14:00 | 21.8 | Mon | School Day | On | On | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0.055249
| 15:00 | 22.4 | Mon | School Day | On | On | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23 | Mon | School Day | On | On | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23.6 | Mon | School Day | On | On | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 23.4 | Mon | School Day | On | On | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 23.1 | Mon | School Day | Off | Off | 22 | 22.11 | -0.11 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 22.7 | Mon | School Day | Off | Off | 22 | 22.07 | -0.07 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 21.4 | Mon | School Day | Off | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 22:00 | 20.1 | Mon | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 23:00 | 19.6 | Mon | School Day | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
Tue, 06/Sep | 24:00 | 18.1 | Tue | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 1:00 | 16.4 | Tue | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 2:00 | 15.8 | Tue | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 3:00 | 14.8 | Tue | School Day | Off | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 4:00 | 13.3 | Tue | School Day | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 5:00 | 13.4 | Tue | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 6:00 | 12.6 | Tue | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 7:00 | 13.1 | Tue | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 8:00 | 12.2 | Tue | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 9:00 | 13.5 | Tue | School Day | On | On | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 2.3481
| 10:00 | 16 | Tue | School Day | On | On | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 1.6575
| 11:00 | 18.4 | Tue | School Day | On | On | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0.99449
| 12:00 | 21.4 | Tue | School Day | On | On | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0.16575
| 13:00 | 23.6 | Tue | School Day | On | On | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 24.5 | Tue | School Day | On | On | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 25.5 | Tue | School Day | On | On | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26 | Tue | School Day | On | On | 22 | 22.4 | -0.4 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 26.3 | Tue | School Day | On | On | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.6 | Tue | School Day | On | On | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 26.4 | Tue | School Day | Off | Off | 22 | 22.44 | -0.44 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 25.1 | Tue | School Day | Off | Off | 22 | 22.31 | -0.31 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.5 | Tue | School Day | Off | Off | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 23.2 | Tue | School Day | Off | Off | 22 | 22.12 | -0.12 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 20.7 | Tue | School Day | Off | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
Wed, 07/Sep | 24:00 | 19.9 | Wed | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 1:00 | 17.8 | Wed | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 2:00 | 17.4 | Wed | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 3:00 | 16.6 | Wed | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 4:00 | 15.9 | Wed | School Day | Off | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 5:00 | 14.9 | Wed | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 6:00 | 14.4 | Wed | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 7:00 | 14 | Wed | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 8:00 | 13.9 | Wed | School Day | On | On | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 2.2376
| 9:00 | 14.8 | Wed | School Day | On | On | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 1.989
| 10:00 | 16.6 | Wed | School Day | On | On | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 1.4917
| 11:00 | 19.5 | Wed | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 12:00 | 22.4 | Wed | School Day | On | On | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 24.6 | Wed | School Day | On | On | 22 | 22.26 | -0.26 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 25.8 | Wed | School Day | On | On | 22 | 22.38 | -0.38 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 27 | Wed | School Day | On | On | 22 | 22.5 | -0.5 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 27.5 | Wed | School Day | On | On | 22 | 22.55 | -0.55 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.3 | Wed | School Day | On | On | 22 | 22.53 | -0.53 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 27 | Wed | School Day | On | On | 22 | 22.5 | -0.5 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 26.3 | Wed | School Day | Off | Off | 22 | 22.43 | -0.43 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.5 | Wed | School Day | Off | Off | 22 | 22.25 | -0.25 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 23.6 | Wed | School Day | Off | Off | 22 | 22.16 | -0.16 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 22.5 | Wed | School Day | Off | Off | 22 | 22.05 | -0.05 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 23:00 | 21.2 | Wed | School Day | Off | Off | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
Thu, 08/Sep | 24:00 | 20.5 | Thu | School Day | Off | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 1:00 | 19.2 | Thu | School Day | Off | Off | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 2:00 | 18.5 | Thu | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 3:00 | 17 | Thu | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 4:00 | 17.1 | Thu | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 5:00 | 17.2 | Thu | School Day | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 6:00 | 17.1 | Thu | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 7:00 | 17 | Thu | School Day | On | On | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 1.3812
| 8:00 | 17.7 | Thu | School Day | On | On | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 1.1879
| 9:00 | 18.1 | Thu | School Day | On | On | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 1.0774
| 10:00 | 18.5 | Thu | School Day | On | On | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0.96686
| 11:00 | 19.9 | Thu | School Day | On | On | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0.58012
| 12:00 | 21.2 | Thu | School Day | On | On | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0.221
| 13:00 | 22.9 | Thu | School Day | On | On | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 23.5 | Thu | School Day | On | On | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.4 | Thu | School Day | On | On | 22 | 22.14 | -0.14 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23 | Thu | School Day | On | On | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 22.6 | Thu | School Day | On | On | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.2 | Thu | School Day | On | On | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 20.9 | Thu | School Day | Off | Off | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 20:00 | 19.5 | Thu | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 21:00 | 18.2 | Thu | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 22:00 | 17.8 | Thu | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 23:00 | 17.6 | Thu | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
Fri, 09/Sep | 24:00 | 17.3 | Fri | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 1:00 | 16.9 | Fri | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 2:00 | 17 | Fri | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 3:00 | 17 | Fri | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 4:00 | 17 | Fri | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 5:00 | 16.6 | Fri | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 6:00 | 16.4 | Fri | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 7:00 | 16.5 | Fri | School Day | On | On | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 1.5194
| 8:00 | 16.2 | Fri | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 9:00 | 15.5 | Fri | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 10:00 | 15.5 | Fri | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 11:00 | 15.4 | Fri | School Day | On | On | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 1.8232
| 12:00 | 15 | Fri | School Day | On | On | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 1.9337
| 13:00 | 15.5 | Fri | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 14:00 | 15.9 | Fri | School Day | On | On | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 1.6851
| 15:00 | 16 | Fri | School Day | On | On | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 1.6575
| 16:00 | 16.4 | Fri | School Day | On | On | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 1.547
| 17:00 | 16.7 | Fri | School Day | On | On | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 1.4641
| 18:00 | 16.6 | Fri | School Day | On | On | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 1.4917
| 19:00 | 16.4 | Fri | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 20:00 | 16.2 | Fri | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 21:00 | 16 | Fri | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 22:00 | 15.8 | Fri | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 23:00 | 15.4 | Fri | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
Sat, 10/Sep | 24:00 | 14.9 | Sat | WE | Off | OFF | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 1:00 | 14.8 | Sat | WE | Off | OFF | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 2:00 | 14.6 | Sat | WE | Off | OFF | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 3:00 | 14.9 | Sat | WE | Off | OFF | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 4:00 | 15.5 | Sat | WE | Off | OFF | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 5:00 | 15.9 | Sat | WE | Off | OFF | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 6:00 | 16.1 | Sat | WE | Off | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 7:00 | 16.2 | Sat | WE | On | OFF | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 8:00 | 16.4 | Sat | WE | On | OFF | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 9:00 | 16.6 | Sat | WE | On | OFF | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 10:00 | 16.9 | Sat | WE | On | OFF | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 11:00 | 17.5 | Sat | WE | On | OFF | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 12:00 | 18.5 | Sat | WE | On | OFF | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 13:00 | 19.2 | Sat | WE | On | OFF | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 14:00 | 19.3 | Sat | WE | On | OFF | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 15:00 | 19.5 | Sat | WE | On | OFF | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 16:00 | 20.5 | Sat | WE | On | OFF | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 17:00 | 20.4 | Sat | WE | On | OFF | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 18:00 | 20.6 | Sat | WE | On | OFF | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 19:00 | 20.6 | Sat | WE | Off | OFF | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 20:00 | 20.2 | Sat | WE | Off | OFF | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 21:00 | 19.4 | Sat | WE | Off | OFF | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 22:00 | 18.7 | Sat | WE | Off | OFF | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 23:00 | 18.5 | Sat | WE | Off | OFF | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
Sun, 11/Sep | 24:00 | 18 | Sun | WE | Off | OFF | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 1:00 | 17.7 | Sun | WE | Off | OFF | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 2:00 | 17.7 | Sun | WE | Off | OFF | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 3:00 | 17.3 | Sun | WE | Off | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 4:00 | 17.3 | Sun | WE | Off | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 5:00 | 17.5 | Sun | WE | Off | OFF | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 6:00 | 17.5 | Sun | WE | Off | OFF | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 7:00 | 17.9 | Sun | WE | On | OFF | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 8:00 | 17.5 | Sun | WE | On | OFF | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 9:00 | 18 | Sun | WE | On | OFF | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 10:00 | 19 | Sun | WE | On | OFF | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 11:00 | 19.4 | Sun | WE | On | OFF | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 12:00 | 19.7 | Sun | WE | On | OFF | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 13:00 | 19.7 | Sun | WE | On | OFF | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 14:00 | 20.1 | Sun | WE | On | OFF | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 15:00 | 20 | Sun | WE | On | OFF | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 16:00 | 20.1 | Sun | WE | On | OFF | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 17:00 | 20.2 | Sun | WE | On | OFF | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 18:00 | 20 | Sun | WE | On | OFF | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 19:00 | 19.8 | Sun | WE | Off | OFF | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 20:00 | 19.6 | Sun | WE | Off | OFF | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 21:00 | 19.1 | Sun | WE | Off | OFF | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 22:00 | 18.5 | Sun | WE | Off | OFF | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 23:00 | 18 | Sun | WE | Off | OFF | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
Mon, 12/Sep | 24:00 | 17.4 | Mon | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 1:00 | 17.4 | Mon | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 2:00 | 17.5 | Mon | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 3:00 | 17 | Mon | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 4:00 | 16.4 | Mon | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 5:00 | 16.4 | Mon | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 6:00 | 16.6 | Mon | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 7:00 | 16.7 | Mon | School Day | On | On | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 1.4641
| 8:00 | 17.1 | Mon | School Day | On | On | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 1.3536
| 9:00 | 17.2 | Mon | School Day | On | On | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 1.326
| 10:00 | 17.8 | Mon | School Day | On | On | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 1.1602
| 11:00 | 18.9 | Mon | School Day | On | On | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0.85637
| 12:00 | 19.2 | Mon | School Day | On | On | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0.77349
| 13:00 | 20.5 | Mon | School Day | On | On | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0.41437
| 14:00 | 21.2 | Mon | School Day | On | On | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0.221
| 15:00 | 21.6 | Mon | School Day | On | On | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0.1105
| 16:00 | 22 | Mon | School Day | On | On | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 22 | Mon | School Day | On | On | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 19.5 | Mon | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 19:00 | 19.9 | Mon | School Day | Off | Off | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 20:00 | 18.8 | Mon | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 21:00 | 17.3 | Mon | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 22:00 | 16.3 | Mon | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 23:00 | 16.7 | Mon | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
Tue, 13/Sep | 24:00 | 16.9 | Tue | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 1:00 | 16.3 | Tue | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 2:00 | 16.1 | Tue | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 3:00 | 16 | Tue | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 4:00 | 16 | Tue | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 5:00 | 15.6 | Tue | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 6:00 | 15.3 | Tue | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 7:00 | 14.8 | Tue | School Day | On | On | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 1.989
| 8:00 | 15 | Tue | School Day | On | On | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 1.9337
| 9:00 | 15.1 | Tue | School Day | On | On | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 1.9061
| 10:00 | 15.8 | Tue | School Day | On | On | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 1.7127
| 11:00 | 16.4 | Tue | School Day | On | On | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 1.547
| 12:00 | 17 | Tue | School Day | On | On | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 1.3812
| 13:00 | 17.9 | Tue | School Day | On | On | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 1.1326
| 14:00 | 18 | Tue | School Day | On | On | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 1.105
| 15:00 | 18.2 | Tue | School Day | On | On | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 1.0497
| 16:00 | 20 | Tue | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 17:00 | 20 | Tue | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 18:00 | 19.8 | Tue | School Day | On | On | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0.60774
| 19:00 | 20.1 | Tue | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 20:00 | 18.7 | Tue | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 21:00 | 17.5 | Tue | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 22:00 | 16.9 | Tue | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 23:00 | 16 | Tue | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
Wed, 14/Sep | 24:00 | 15.3 | Wed | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 1:00 | 14.3 | Wed | School Day | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 2:00 | 14.8 | Wed | School Day | Off | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 3:00 | 14.5 | Wed | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 4:00 | 13.5 | Wed | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 5:00 | 13.5 | Wed | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 6:00 | 12.3 | Wed | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 7:00 | 10 | Wed | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 8:00 | 10.8 | Wed | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 9:00 | 11.4 | Wed | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 10:00 | 13.1 | Wed | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 11:00 | 14.5 | Wed | School Day | On | On | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 2.0719
| 12:00 | 15.7 | Wed | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 13:00 | 15.8 | Wed | School Day | On | On | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 1.7127
| 14:00 | 15.9 | Wed | School Day | On | On | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 1.6851
| 15:00 | 15.8 | Wed | School Day | On | On | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 1.7127
| 16:00 | 14.5 | Wed | School Day | On | On | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 2.0719
| 17:00 | 13.8 | Wed | School Day | On | On | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 2.2652
| 18:00 | 12.9 | Wed | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 19:00 | 14 | Wed | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 20:00 | 15.4 | Wed | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 21:00 | 15.3 | Wed | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 22:00 | 16 | Wed | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 23:00 | 17.4 | Wed | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
Thu, 15/Sep | 24:00 | 17.6 | Thu | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 1:00 | 17.6 | Thu | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 2:00 | 17.4 | Thu | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 3:00 | 17.1 | Thu | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 4:00 | 17 | Thu | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 5:00 | 16.5 | Thu | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 6:00 | 16 | Thu | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 7:00 | 15.9 | Thu | School Day | On | On | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 1.6851
| 8:00 | 15.9 | Thu | School Day | On | On | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 1.6851
| 9:00 | 16.2 | Thu | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 10:00 | 16.3 | Thu | School Day | On | On | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 1.5746
| 11:00 | 17.2 | Thu | School Day | On | On | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 1.326
| 12:00 | 17.7 | Thu | School Day | On | On | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 1.1879
| 13:00 | 19.7 | Thu | School Day | On | On | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0.63537
| 14:00 | 20.6 | Thu | School Day | On | On | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0.38675
| 15:00 | 21.8 | Thu | School Day | On | On | 22 | 21.98 | 0.02 | 1.7 | 0.038202 | 0.25 | 1035 | 0.017047 | 0.055249
| 16:00 | 21.2 | Thu | School Day | On | On | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0.221
| 17:00 | 20.9 | Thu | School Day | On | On | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0.30387
| 18:00 | 22.4 | Thu | School Day | On | On | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 21 | Thu | School Day | Off | Off | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 20:00 | 20.6 | Thu | School Day | Off | Off | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 21:00 | 20.2 | Thu | School Day | Off | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 22:00 | 20.3 | Thu | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 23:00 | 20.4 | Thu | School Day | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
Fri, 16/Sep | 24:00 | 20.5 | Fri | School Day | Off | Off | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 1:00 | 20.3 | Fri | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 2:00 | 20 | Fri | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 3:00 | 20 | Fri | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 4:00 | 19.8 | Fri | School Day | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 5:00 | 18.8 | Fri | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 6:00 | 17.1 | Fri | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 7:00 | 17 | Fri | School Day | On | On | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 1.3812
| 8:00 | 17.4 | Fri | School Day | On | On | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 1.2707
| 9:00 | 18 | Fri | School Day | On | On | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 1.105
| 10:00 | 18.5 | Fri | School Day | On | On | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0.96686
| 11:00 | 19.5 | Fri | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 12:00 | 19.8 | Fri | School Day | On | On | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0.60774
| 13:00 | 18.8 | Fri | School Day | On | On | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0.88399
| 14:00 | 20 | Fri | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 15:00 | 21.6 | Fri | School Day | On | On | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0.1105
| 16:00 | 22.4 | Fri | School Day | On | On | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 22.1 | Fri | School Day | On | On | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 21.7 | Fri | School Day | On | On | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0.082874
| 19:00 | 21.4 | Fri | School Day | Off | Off | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0
| 20:00 | 20.7 | Fri | School Day | Off | Off | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 21:00 | 20.3 | Fri | School Day | Off | Off | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 22:00 | 20.4 | Fri | School Day | Off | Off | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 23:00 | 19.5 | Fri | School Day | Off | Off | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
Sat, 17/Sep | 24:00 | 19.8 | Sat | WE | Off | OFF | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 1:00 | 19.7 | Sat | WE | Off | OFF | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 2:00 | 19.1 | Sat | WE | Off | OFF | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 3:00 | 19.1 | Sat | WE | Off | OFF | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 4:00 | 19.2 | Sat | WE | Off | OFF | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 5:00 | 19.3 | Sat | WE | Off | OFF | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 6:00 | 19.2 | Sat | WE | Off | OFF | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 7:00 | 19.2 | Sat | WE | On | OFF | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 8:00 | 19.3 | Sat | WE | On | OFF | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 9:00 | 19.5 | Sat | WE | On | OFF | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 10:00 | 19.6 | Sat | WE | On | OFF | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 11:00 | 20.1 | Sat | WE | On | OFF | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 12:00 | 20.6 | Sat | WE | On | OFF | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 13:00 | 20.4 | Sat | WE | On | OFF | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0
| 14:00 | 21 | Sat | WE | On | OFF | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 15:00 | 21.2 | Sat | WE | On | OFF | 22 | 21.92 | 0.08 | 1.7 | 0.15281 | 0.25 | 1035 | 0.068189 | 0
| 16:00 | 21.9 | Sat | WE | On | OFF | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 17:00 | 21.6 | Sat | WE | On | OFF | 22 | 21.96 | 0.04 | 1.7 | 0.076404 | 0.25 | 1035 | 0.034095 | 0
| 18:00 | 21.5 | Sat | WE | On | OFF | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0
| 19:00 | 20.9 | Sat | WE | Off | OFF | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0
| 20:00 | 20.5 | Sat | WE | Off | OFF | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 21:00 | 19.9 | Sat | WE | Off | OFF | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0
| 22:00 | 19 | Sat | WE | Off | OFF | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 23:00 | 18.5 | Sat | WE | Off | OFF | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
Sun, 18/Sep | 24:00 | 17.3 | Sun | WE | Off | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 1:00 | 16.8 | Sun | WE | Off | OFF | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 2:00 | 16.4 | Sun | WE | Off | OFF | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 3:00 | 15.8 | Sun | WE | Off | OFF | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 4:00 | 15.2 | Sun | WE | Off | OFF | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 5:00 | 15 | Sun | WE | Off | OFF | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 6:00 | 15.1 | Sun | WE | Off | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 7:00 | 16.3 | Sun | WE | On | OFF | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 8:00 | 17 | Sun | WE | On | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 9:00 | 17.5 | Sun | WE | On | OFF | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 10:00 | 19 | Sun | WE | On | OFF | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 11:00 | 20.6 | Sun | WE | On | OFF | 22 | 21.86 | 0.14 | 1.7 | 0.26741 | 0.25 | 1035 | 0.11933 | 0
| 12:00 | 21 | Sun | WE | On | OFF | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 13:00 | 22.8 | Sun | WE | On | OFF | 22 | 22.08 | -0.08 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 23.7 | Sun | WE | On | OFF | 22 | 22.17 | -0.17 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23.8 | Sun | WE | On | OFF | 22 | 22.18 | -0.18 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23.8 | Sun | WE | On | OFF | 22 | 22.18 | -0.18 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23.5 | Sun | WE | On | OFF | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.1 | Sun | WE | On | OFF | 22 | 22.01 | -0.01 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 21.9 | Sun | WE | Off | OFF | 22 | 21.99 | 0.01 | 1.7 | 0.019101 | 0.25 | 1035 | 0.0085237 | 0
| 20:00 | 21 | Sun | WE | Off | OFF | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 21:00 | 20 | Sun | WE | Off | OFF | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 22:00 | 19.6 | Sun | WE | Off | OFF | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 23:00 | 19.4 | Sun | WE | Off | OFF | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
Mon, 19/Sep | 24:00 | 19.4 | Mon | School Day | Off | Off | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0
| 1:00 | 18.7 | Mon | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 2:00 | 18.5 | Mon | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 3:00 | 18.1 | Mon | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 4:00 | 17.1 | Mon | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 5:00 | 16.4 | Mon | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 6:00 | 16.2 | Mon | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 7:00 | 16.4 | Mon | School Day | On | On | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 1.547
| 8:00 | 16.3 | Mon | School Day | On | On | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 1.5746
| 9:00 | 16 | Mon | School Day | On | On | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 1.6575
| 10:00 | 15.9 | Mon | School Day | On | On | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 1.6851
| 11:00 | 17.7 | Mon | School Day | On | On | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 1.1879
| 12:00 | 19.1 | Mon | School Day | On | On | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0.80112
| 13:00 | 20.7 | Mon | School Day | On | On | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0.35912
| 14:00 | 21 | Mon | School Day | On | On | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0.27625
| 15:00 | 20 | Mon | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 16:00 | 21.5 | Mon | School Day | On | On | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0.13812
| 17:00 | 21.3 | Mon | School Day | On | On | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0.19337
| 18:00 | 21.7 | Mon | School Day | On | On | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0.082874
| 19:00 | 20 | Mon | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 20:00 | 18.9 | Mon | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 21:00 | 17.4 | Mon | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 22:00 | 16.6 | Mon | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 23:00 | 15.6 | Mon | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
Tue, 20/Sep | 24:00 | 14.9 | Tue | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 1:00 | 14.3 | Tue | School Day | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 2:00 | 12.9 | Tue | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 3:00 | 13.1 | Tue | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 4:00 | 13.5 | Tue | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 5:00 | 14.1 | Tue | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 6:00 | 13.6 | Tue | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 7:00 | 13.6 | Tue | School Day | On | On | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 2.3205
| 8:00 | 13.7 | Tue | School Day | On | On | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 2.2928
| 9:00 | 15.4 | Tue | School Day | On | On | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 1.8232
| 10:00 | 18 | Tue | School Day | On | On | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 1.105
| 11:00 | 19.9 | Tue | School Day | On | On | 22 | 21.79 | 0.21 | 1.7 | 0.40112 | 0.25 | 1035 | 0.179 | 0.58012
| 12:00 | 22 | Tue | School Day | On | On | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 22 | Tue | School Day | On | On | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 22.4 | Tue | School Day | On | On | 22 | 22.04 | -0.04 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23 | Tue | School Day | On | On | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23 | Tue | School Day | On | On | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23 | Tue | School Day | On | On | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.2 | Tue | School Day | On | On | 22 | 22.02 | -0.02 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 21.3 | Tue | School Day | Off | Off | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 20:00 | 20 | Tue | School Day | Off | Off | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0
| 21:00 | 18.9 | Tue | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 22:00 | 18 | Tue | School Day | Off | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 23:00 | 17.2 | Tue | School Day | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
Wed, 21/Sep | 24:00 | 16.9 | Wed | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 1:00 | 15 | Wed | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 2:00 | 13.7 | Wed | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 3:00 | 14.4 | Wed | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 4:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 5:00 | 13.5 | Wed | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 6:00 | 13.2 | Wed | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 7:00 | 14 | Wed | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 8:00 | 14.2 | Wed | School Day | On | On | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 2.1547
| 9:00 | 15.6 | Wed | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 10:00 | 18.2 | Wed | School Day | On | On | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 1.0497
| 11:00 | 21.4 | Wed | School Day | On | On | 22 | 21.94 | 0.06 | 1.7 | 0.11461 | 0.25 | 1035 | 0.051142 | 0.16575
| 12:00 | 24.2 | Wed | School Day | On | On | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 13:00 | 25.9 | Wed | School Day | On | On | 22 | 22.39 | -0.39 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 14:00 | 26.9 | Wed | School Day | On | On | 22 | 22.49 | -0.49 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 26.2 | Wed | School Day | On | On | 22 | 22.42 | -0.42 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 26.6 | Wed | School Day | On | On | 22 | 22.46 | -0.46 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 27.6 | Wed | School Day | On | On | 22 | 22.56 | -0.56 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 26.5 | Wed | School Day | On | On | 22 | 22.45 | -0.45 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 25.5 | Wed | School Day | Off | Off | 22 | 22.35 | -0.35 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 24.2 | Wed | School Day | Off | Off | 22 | 22.22 | -0.22 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 21:00 | 22.6 | Wed | School Day | Off | Off | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 22:00 | 19.6 | Wed | School Day | Off | Off | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0
| 23:00 | 20.1 | Wed | School Day | Off | Off | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
Thu, 22/Sep | 24:00 | 19.8 | Thu | School Day | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 1:00 | 19.8 | Thu | School Day | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 2:00 | 19 | Thu | School Day | Off | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 3:00 | 19 | Thu | School Day | Off | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 4:00 | 18.7 | Thu | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 5:00 | 18.5 | Thu | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 6:00 | 18 | Thu | School Day | Off | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 7:00 | 18.7 | Thu | School Day | On | On | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0.91161
| 8:00 | 19.1 | Thu | School Day | On | On | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0.80112
| 9:00 | 19.5 | Thu | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 10:00 | 19.3 | Thu | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 11:00 | 19 | Thu | School Day | On | On | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0.82874
| 12:00 | 19.1 | Thu | School Day | On | On | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0.80112
| 13:00 | 19.6 | Thu | School Day | On | On | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0.66299
| 14:00 | 19.7 | Thu | School Day | On | On | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0.63537
| 15:00 | 19.4 | Thu | School Day | On | On | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0.71824
| 16:00 | 19 | Thu | School Day | On | On | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0.82874
| 17:00 | 19.7 | Thu | School Day | On | On | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0.63537
| 18:00 | 18.2 | Thu | School Day | On | On | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 1.0497
| 19:00 | 18.7 | Thu | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 20:00 | 17.2 | Thu | School Day | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 21:00 | 16.7 | Thu | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 22:00 | 15.9 | Thu | School Day | Off | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 23:00 | 15.6 | Thu | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
Fri, 23/Sep | 24:00 | 15.3 | Fri | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 1:00 | 14.2 | Fri | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 2:00 | 13.9 | Fri | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 3:00 | 13.8 | Fri | School Day | Off | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 4:00 | 13.3 | Fri | School Day | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 5:00 | 13 | Fri | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 6:00 | 12.2 | Fri | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 7:00 | 12.5 | Fri | School Day | On | On | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 2.6243
| 8:00 | 12.2 | Fri | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 9:00 | 11.4 | Fri | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 10:00 | 12.5 | Fri | School Day | On | On | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 2.6243
| 11:00 | 14 | Fri | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 12:00 | 16 | Fri | School Day | On | On | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 1.6575
| 13:00 | 17.6 | Fri | School Day | On | On | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 1.2155
| 14:00 | 18 | Fri | School Day | On | On | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 1.105
| 15:00 | 18.8 | Fri | School Day | On | On | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0.88399
| 16:00 | 18.9 | Fri | School Day | On | On | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0.85637
| 17:00 | 19.5 | Fri | School Day | On | On | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0.69062
| 18:00 | 19.3 | Fri | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 19:00 | 19.1 | Fri | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 20:00 | 18.7 | Fri | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 21:00 | 18.7 | Fri | School Day | Off | Off | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0
| 22:00 | 18.2 | Fri | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 23:00 | 17.7 | Fri | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
Sat, 24/Sep | 24:00 | 17 | Sat | WE | Off | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 1:00 | 16.6 | Sat | WE | Off | OFF | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 2:00 | 16.4 | Sat | WE | Off | OFF | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 3:00 | 16 | Sat | WE | Off | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 4:00 | 15.5 | Sat | WE | Off | OFF | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 5:00 | 15.7 | Sat | WE | Off | OFF | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 6:00 | 15.4 | Sat | WE | Off | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 7:00 | 15.2 | Sat | WE | On | OFF | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 8:00 | 14.7 | Sat | WE | On | OFF | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 9:00 | 14.2 | Sat | WE | On | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 10:00 | 14.9 | Sat | WE | On | OFF | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 11:00 | 17.1 | Sat | WE | On | OFF | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 12:00 | 19.8 | Sat | WE | On | OFF | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 13:00 | 21.3 | Sat | WE | On | OFF | 22 | 21.93 | 0.07 | 1.7 | 0.13371 | 0.25 | 1035 | 0.059666 | 0
| 14:00 | 20.8 | Sat | WE | On | OFF | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0
| 15:00 | 21.7 | Sat | WE | On | OFF | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 16:00 | 21.7 | Sat | WE | On | OFF | 22 | 21.97 | 0.03 | 1.7 | 0.057303 | 0.25 | 1035 | 0.025571 | 0
| 17:00 | 22.3 | Sat | WE | On | OFF | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.3 | Sat | WE | On | OFF | 22 | 22.03 | -0.03 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 21 | Sat | WE | Off | OFF | 22 | 21.9 | 0.1 | 1.7 | 0.19101 | 0.25 | 1035 | 0.085237 | 0
| 20:00 | 20.5 | Sat | WE | Off | OFF | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0
| 21:00 | 20.3 | Sat | WE | Off | OFF | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 22:00 | 19.5 | Sat | WE | Off | OFF | 22 | 21.75 | 0.25 | 1.7 | 0.47753 | 0.25 | 1035 | 0.21309 | 0
| 23:00 | 18.8 | Sat | WE | Off | OFF | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
Sun, 25/Sep | 24:00 | 18 | Sun | WE | Off | OFF | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 1:00 | 17.2 | Sun | WE | Off | OFF | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 2:00 | 16.6 | Sun | WE | Off | OFF | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 3:00 | 15.2 | Sun | WE | Off | OFF | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 4:00 | 14.2 | Sun | WE | Off | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 5:00 | 14.1 | Sun | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 6:00 | 13 | Sun | WE | Off | OFF | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 7:00 | 12.5 | Sun | WE | On | OFF | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 8:00 | 12 | Sun | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 9:00 | 11.9 | Sun | WE | On | OFF | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 10:00 | 12.2 | Sun | WE | On | OFF | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 11:00 | 14.2 | Sun | WE | On | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 12:00 | 18.3 | Sun | WE | On | OFF | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 13:00 | 20.3 | Sun | WE | On | OFF | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0
| 14:00 | 22 | Sun | WE | On | OFF | 22 | 22 | 0 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 15:00 | 23 | Sun | WE | On | OFF | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 16:00 | 23 | Sun | WE | On | OFF | 22 | 22.1 | -0.1 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 17:00 | 23.5 | Sun | WE | On | OFF | 22 | 22.15 | -0.15 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 18:00 | 22.9 | Sun | WE | On | OFF | 22 | 22.09 | -0.09 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 19:00 | 22.6 | Sun | WE | Off | OFF | 22 | 22.06 | -0.06 | 1.7 | 0 | 0.25 | 1035 | 0 | 0
| 20:00 | 20.7 | Sun | WE | Off | OFF | 22 | 21.87 | 0.13 | 1.7 | 0.24831 | 0.25 | 1035 | 0.11081 | 0
| 21:00 | 18.9 | Sun | WE | Off | OFF | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 22:00 | 18.3 | Sun | WE | Off | OFF | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 23:00 | 16.7 | Sun | WE | Off | OFF | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
Mon, 26/Sep | 24:00 | 17.5 | Mon | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 1:00 | 15.2 | Mon | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 2:00 | 14 | Mon | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 3:00 | 14.2 | Mon | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 4:00 | 13.4 | Mon | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 5:00 | 12.6 | Mon | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 6:00 | 12.5 | Mon | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 7:00 | 13 | Mon | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 8:00 | 14 | Mon | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 9:00 | 14.7 | Mon | School Day | On | On | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 2.0166
| 10:00 | 15.4 | Mon | School Day | On | On | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 1.8232
| 11:00 | 16 | Mon | School Day | On | On | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 1.6575
| 12:00 | 17.2 | Mon | School Day | On | On | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 1.326
| 13:00 | 18.1 | Mon | School Day | On | On | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 1.0774
| 14:00 | 19.6 | Mon | School Day | On | On | 22 | 21.76 | 0.24 | 1.7 | 0.45842 | 0.25 | 1035 | 0.20457 | 0.66299
| 15:00 | 20.4 | Mon | School Day | On | On | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0.44199
| 16:00 | 20 | Mon | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 17:00 | 20.4 | Mon | School Day | On | On | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0.44199
| 18:00 | 20.5 | Mon | School Day | On | On | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0.41437
| 19:00 | 20.2 | Mon | School Day | Off | Off | 22 | 21.82 | 0.18 | 1.7 | 0.34382 | 0.25 | 1035 | 0.15343 | 0
| 20:00 | 19.7 | Mon | School Day | Off | Off | 22 | 21.77 | 0.23 | 1.7 | 0.43932 | 0.25 | 1035 | 0.19604 | 0
| 21:00 | 19 | Mon | School Day | Off | Off | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 22:00 | 18.8 | Mon | School Day | Off | Off | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0
| 23:00 | 18.5 | Mon | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
Tue, 27/Sep | 24:00 | 18.2 | Tue | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 1:00 | 18.1 | Tue | School Day | Off | Off | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 2:00 | 17.5 | Tue | School Day | Off | Off | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 3:00 | 17.4 | Tue | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 4:00 | 17.1 | Tue | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 5:00 | 16.9 | Tue | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 6:00 | 16.2 | Tue | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 7:00 | 16.1 | Tue | School Day | On | On | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 1.6299
| 8:00 | 16.3 | Tue | School Day | On | On | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 1.5746
| 9:00 | 16.2 | Tue | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 10:00 | 16.1 | Tue | School Day | On | On | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 1.6299
| 11:00 | 16.8 | Tue | School Day | On | On | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 1.4365
| 12:00 | 17.3 | Tue | School Day | On | On | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 1.2984
| 13:00 | 18 | Tue | School Day | On | On | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 1.105
| 14:00 | 19 | Tue | School Day | On | On | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0.82874
| 15:00 | 18.4 | Tue | School Day | On | On | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0.99449
| 16:00 | 18.5 | Tue | School Day | On | On | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0.96686
| 17:00 | 18.6 | Tue | School Day | On | On | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0.93924
| 18:00 | 18.1 | Tue | School Day | On | On | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 1.0774
| 19:00 | 17.9 | Tue | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 20:00 | 16.1 | Tue | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 21:00 | 16.1 | Tue | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 22:00 | 15.4 | Tue | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 23:00 | 14.8 | Tue | School Day | Off | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
Wed, 28/Sep | 24:00 | 14.2 | Wed | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 1:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 2:00 | 13.7 | Wed | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 3:00 | 13.5 | Wed | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 4:00 | 12.9 | Wed | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 5:00 | 12.6 | Wed | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 6:00 | 12.6 | Wed | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 7:00 | 13 | Wed | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 8:00 | 12.8 | Wed | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 9:00 | 13 | Wed | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 10:00 | 13.4 | Wed | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 11:00 | 14.1 | Wed | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 12:00 | 15 | Wed | School Day | On | On | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 1.9337
| 13:00 | 15.6 | Wed | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 14:00 | 16.2 | Wed | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 15:00 | 16.2 | Wed | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 16:00 | 17.4 | Wed | School Day | On | On | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 1.2707
| 17:00 | 17.3 | Wed | School Day | On | On | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 1.2984
| 18:00 | 17.3 | Wed | School Day | On | On | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 1.2984
| 19:00 | 16.9 | Wed | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 20:00 | 16.4 | Wed | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 21:00 | 15.3 | Wed | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 22:00 | 14.2 | Wed | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 23:00 | 13.1 | Wed | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
Thu, 29/Sep | 24:00 | 12.2 | Thu | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 1:00 | 11.4 | Thu | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 2:00 | 11 | Thu | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 3:00 | 10.7 | Thu | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 4:00 | 10.2 | Thu | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 5:00 | 9.4 | Thu | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 6:00 | 10 | Thu | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 7:00 | 8.9 | Thu | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 8:00 | 8.9 | Thu | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 9:00 | 8.8 | Thu | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 10:00 | 10.7 | Thu | School Day | On | On | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 3.1216
| 11:00 | 13.2 | Thu | School Day | On | On | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 2.431
| 12:00 | 15.5 | Thu | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 13:00 | 17 | Thu | School Day | On | On | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 1.3812
| 14:00 | 17.7 | Thu | School Day | On | On | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 1.1879
| 15:00 | 18.8 | Thu | School Day | On | On | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0.88399
| 16:00 | 19 | Thu | School Day | On | On | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0.82874
| 17:00 | 18.7 | Thu | School Day | On | On | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0.91161
| 18:00 | 18.5 | Thu | School Day | On | On | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0.96686
| 19:00 | 18 | Thu | School Day | Off | Off | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 20:00 | 17.1 | Thu | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 21:00 | 16.2 | Thu | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 22:00 | 15.9 | Thu | School Day | Off | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 23:00 | 15.2 | Thu | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
Fri, 30/Sep | 24:00 | 14.1 | Fri | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 1:00 | 12.9 | Fri | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 2:00 | 12.1 | Fri | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 3:00 | 11.8 | Fri | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 4:00 | 12.1 | Fri | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 5:00 | 12.6 | Fri | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 6:00 | 12.6 | Fri | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 7:00 | 13.4 | Fri | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 8:00 | 13.8 | Fri | School Day | On | On | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 2.2652
| 9:00 | 13.4 | Fri | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 10:00 | 14 | Fri | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 11:00 | 14 | Fri | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 12:00 | 14.3 | Fri | School Day | On | On | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 2.1271
| 13:00 | 15 | Fri | School Day | On | On | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 1.9337
| 14:00 | 15.7 | Fri | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 15:00 | 16.3 | Fri | School Day | On | On | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 1.5746
| 16:00 | 16.3 | Fri | School Day | On | On | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 1.5746
| 17:00 | 16.4 | Fri | School Day | On | On | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 1.547
| 18:00 | 16.3 | Fri | School Day | On | On | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 1.5746
| 19:00 | 16.5 | Fri | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 20:00 | 16 | Fri | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 21:00 | 15.2 | Fri | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 22:00 | 14.5 | Fri | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 23:00 | 14.2 | Fri | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
Sat, 01/Oct | 24:00 | 13.5 | Sat | WE | Off | OFF | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 1:00 | 14.1 | Sat | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 2:00 | 14.1 | Sat | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 3:00 | 14 | Sat | WE | Off | OFF | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 4:00 | 14.1 | Sat | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 5:00 | 14.1 | Sat | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 6:00 | 14.1 | Sat | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 7:00 | 13.6 | Sat | WE | On | OFF | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 8:00 | 13.5 | Sat | WE | On | OFF | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 9:00 | 13.5 | Sat | WE | On | OFF | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 10:00 | 14 | Sat | WE | On | OFF | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 11:00 | 14.5 | Sat | WE | On | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 12:00 | 14.8 | Sat | WE | On | OFF | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 13:00 | 15.5 | Sat | WE | On | OFF | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 14:00 | 15.7 | Sat | WE | On | OFF | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 15:00 | 16.1 | Sat | WE | On | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 16:00 | 16.1 | Sat | WE | On | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 17:00 | 16.2 | Sat | WE | On | OFF | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 18:00 | 16.3 | Sat | WE | On | OFF | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 19:00 | 16 | Sat | WE | Off | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 20:00 | 15.5 | Sat | WE | Off | OFF | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 21:00 | 15 | Sat | WE | Off | OFF | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 22:00 | 14.7 | Sat | WE | Off | OFF | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 23:00 | 14.5 | Sat | WE | Off | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
Sun, 02/Oct | 24:00 | 14.5 | Sun | WE | Off | OFF | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 1:00 | 14 | Sun | WE | Off | OFF | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 2:00 | 14 | Sun | WE | Off | OFF | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 3:00 | 13.8 | Sun | WE | Off | OFF | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 4:00 | 13.6 | Sun | WE | Off | OFF | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 5:00 | 13.4 | Sun | WE | Off | OFF | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 6:00 | 13.2 | Sun | WE | Off | OFF | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 7:00 | 13.3 | Sun | WE | On | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 8:00 | 13.3 | Sun | WE | On | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 9:00 | 13.4 | Sun | WE | On | OFF | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 10:00 | 13.8 | Sun | WE | On | OFF | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 11:00 | 14 | Sun | WE | On | OFF | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 12:00 | 14.4 | Sun | WE | On | OFF | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 13:00 | 15 | Sun | WE | On | OFF | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 14:00 | 15.3 | Sun | WE | On | OFF | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 15:00 | 15.4 | Sun | WE | On | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 16:00 | 16.4 | Sun | WE | On | OFF | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 17:00 | 16.7 | Sun | WE | On | OFF | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 18:00 | 17.3 | Sun | WE | On | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 19:00 | 16.7 | Sun | WE | Off | OFF | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 20:00 | 15.3 | Sun | WE | Off | OFF | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 21:00 | 14.3 | Sun | WE | Off | OFF | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 22:00 | 13.6 | Sun | WE | Off | OFF | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 23:00 | 12.4 | Sun | WE | Off | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
Mon, 03/Oct | 24:00 | 11.2 | Mon | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 1:00 | 10.2 | Mon | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 2:00 | 9.1 | Mon | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 3:00 | 8 | Mon | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 4:00 | 7.1 | Mon | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 5:00 | 6.9 | Mon | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 6:00 | 6.8 | Mon | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 7:00 | 7.7 | Mon | School Day | On | On | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 3.9503
| 8:00 | 8.8 | Mon | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 9:00 | 9.5 | Mon | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 10:00 | 10.7 | Mon | School Day | On | On | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 3.1216
| 11:00 | 11.8 | Mon | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 12:00 | 12.9 | Mon | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 13:00 | 13.9 | Mon | School Day | On | On | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 2.2376
| 14:00 | 14.8 | Mon | School Day | On | On | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 1.989
| 15:00 | 15.7 | Mon | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 16:00 | 16.1 | Mon | School Day | On | On | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 1.6299
| 17:00 | 16.1 | Mon | School Day | On | On | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 1.6299
| 18:00 | 17 | Mon | School Day | On | On | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 1.3812
| 19:00 | 16.1 | Mon | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 20:00 | 15.3 | Mon | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 21:00 | 15 | Mon | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 22:00 | 15.2 | Mon | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 23:00 | 15 | Mon | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
Tue, 04/Oct | 24:00 | 15.2 | Tue | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 1:00 | 15 | Tue | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 2:00 | 15.1 | Tue | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 3:00 | 14.9 | Tue | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 4:00 | 14.6 | Tue | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 5:00 | 14.4 | Tue | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 6:00 | 14.5 | Tue | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 7:00 | 14.1 | Tue | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 8:00 | 13 | Tue | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 9:00 | 12.9 | Tue | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 10:00 | 13.7 | Tue | School Day | On | On | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 2.2928
| 11:00 | 15.6 | Tue | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 12:00 | 17.2 | Tue | School Day | On | On | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 1.326
| 13:00 | 18.4 | Tue | School Day | On | On | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0.99449
| 14:00 | 19.3 | Tue | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 15:00 | 20 | Tue | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 16:00 | 20 | Tue | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 17:00 | 20 | Tue | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 18:00 | 19.3 | Tue | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 19:00 | 17.8 | Tue | School Day | Off | Off | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 0
| 20:00 | 15.9 | Tue | School Day | Off | Off | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 21:00 | 14.2 | Tue | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 22:00 | 13.1 | Tue | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 23:00 | 11.4 | Tue | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
Wed, 05/Oct | 24:00 | 13.2 | Wed | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 1:00 | 11 | Wed | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 2:00 | 10.2 | Wed | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 3:00 | 9.1 | Wed | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 4:00 | 10.2 | Wed | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 5:00 | 9.5 | Wed | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 6:00 | 8.8 | Wed | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 7:00 | 8.6 | Wed | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 8:00 | 9.3 | Wed | School Day | On | On | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 3.5083
| 9:00 | 8.3 | Wed | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 10:00 | 12.7 | Wed | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 11:00 | 15.7 | Wed | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 12:00 | 18.6 | Wed | School Day | On | On | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0.93924
| 13:00 | 20 | Wed | School Day | On | On | 22 | 21.8 | 0.2 | 1.7 | 0.38202 | 0.25 | 1035 | 0.17047 | 0.55249
| 14:00 | 20.8 | Wed | School Day | On | On | 22 | 21.88 | 0.12 | 1.7 | 0.22921 | 0.25 | 1035 | 0.10228 | 0.3315
| 15:00 | 21.5 | Wed | School Day | On | On | 22 | 21.95 | 0.05 | 1.7 | 0.095505 | 0.25 | 1035 | 0.042618 | 0.13812
| 16:00 | 20.1 | Wed | School Day | On | On | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0.52487
| 17:00 | 16.9 | Wed | School Day | On | On | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 1.4089
| 18:00 | 17 | Wed | School Day | On | On | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 1.3812
| 19:00 | 15.3 | Wed | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 20:00 | 14.8 | Wed | School Day | Off | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 21:00 | 14.4 | Wed | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 22:00 | 13.2 | Wed | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 23:00 | 12.2 | Wed | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
Thu, 06/Oct | 24:00 | 11.1 | Thu | School Day | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 1:00 | 10.6 | Thu | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 2:00 | 9.4 | Thu | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 3:00 | 7.7 | Thu | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 4:00 | 7 | Thu | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 5:00 | 6.6 | Thu | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 6:00 | 6.4 | Thu | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 7:00 | 8.5 | Thu | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 8:00 | 8.8 | Thu | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 9:00 | 9.5 | Thu | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 10:00 | 11.1 | Thu | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 11:00 | 11.9 | Thu | School Day | On | On | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 2.7901
| 12:00 | 13 | Thu | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 13:00 | 13.7 | Thu | School Day | On | On | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 2.2928
| 14:00 | 14.1 | Thu | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 15:00 | 14.9 | Thu | School Day | On | On | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 1.9614
| 16:00 | 15.3 | Thu | School Day | On | On | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 1.8509
| 17:00 | 16.4 | Thu | School Day | On | On | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 1.547
| 18:00 | 16.2 | Thu | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 19:00 | 16.6 | Thu | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 20:00 | 16.9 | Thu | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 21:00 | 16.9 | Thu | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 22:00 | 16.5 | Thu | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 23:00 | 16.2 | Thu | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
Fri, 07/Oct | 24:00 | 15.5 | Fri | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 1:00 | 14.9 | Fri | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 2:00 | 13.6 | Fri | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 3:00 | 12.9 | Fri | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 4:00 | 12.8 | Fri | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 5:00 | 12.5 | Fri | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 6:00 | 12.9 | Fri | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 7:00 | 12.9 | Fri | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 8:00 | 13 | Fri | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 9:00 | 12.7 | Fri | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 10:00 | 13 | Fri | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 11:00 | 13.6 | Fri | School Day | On | On | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 2.3205
| 12:00 | 13.8 | Fri | School Day | On | On | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 2.2652
| 13:00 | 14.3 | Fri | School Day | On | On | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 2.1271
| 14:00 | 14.1 | Fri | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 15:00 | 13.1 | Fri | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 16:00 | 14.1 | Fri | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 17:00 | 14.6 | Fri | School Day | On | On | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 2.0442
| 18:00 | 14.9 | Fri | School Day | On | On | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 1.9614
| 19:00 | 14.5 | Fri | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 20:00 | 14.1 | Fri | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 21:00 | 13.8 | Fri | School Day | Off | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 22:00 | 13.8 | Fri | School Day | Off | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 23:00 | 14 | Fri | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
Sat, 08/Oct | 24:00 | 14.1 | Sat | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 1:00 | 12.4 | Sat | WE | Off | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 2:00 | 12 | Sat | WE | Off | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 3:00 | 11.8 | Sat | WE | Off | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 4:00 | 11.6 | Sat | WE | Off | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 5:00 | 10.6 | Sat | WE | Off | OFF | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 6:00 | 10.5 | Sat | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 7:00 | 10 | Sat | WE | On | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 8:00 | 9.8 | Sat | WE | On | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 9:00 | 10.1 | Sat | WE | On | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 10:00 | 11.3 | Sat | WE | On | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 11:00 | 12.3 | Sat | WE | On | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 12:00 | 13.8 | Sat | WE | On | OFF | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 13:00 | 14.3 | Sat | WE | On | OFF | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 14:00 | 15.5 | Sat | WE | On | OFF | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 15:00 | 16 | Sat | WE | On | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 16:00 | 15.7 | Sat | WE | On | OFF | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 17:00 | 16 | Sat | WE | On | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 18:00 | 15.5 | Sat | WE | On | OFF | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 19:00 | 15.2 | Sat | WE | Off | OFF | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 20:00 | 14.8 | Sat | WE | Off | OFF | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 21:00 | 13 | Sat | WE | Off | OFF | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 22:00 | 12.1 | Sat | WE | Off | OFF | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 23:00 | 11.1 | Sat | WE | Off | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
Sun, 09/Oct | 24:00 | 10.5 | Sun | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 1:00 | 7.8 | Sun | WE | Off | OFF | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 2:00 | 8.7 | Sun | WE | Off | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 3:00 | 8.8 | Sun | WE | Off | OFF | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 4:00 | 9.4 | Sun | WE | Off | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 5:00 | 10.1 | Sun | WE | Off | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 6:00 | 11.2 | Sun | WE | Off | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 7:00 | 11.4 | Sun | WE | On | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 8:00 | 12.1 | Sun | WE | On | OFF | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 9:00 | 12.7 | Sun | WE | On | OFF | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 10:00 | 13.8 | Sun | WE | On | OFF | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 11:00 | 14.1 | Sun | WE | On | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 12:00 | 14.1 | Sun | WE | On | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 13:00 | 13.7 | Sun | WE | On | OFF | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 14:00 | 15.2 | Sun | WE | On | OFF | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 15:00 | 16.2 | Sun | WE | On | OFF | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 16:00 | 16.1 | Sun | WE | On | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 17:00 | 16 | Sun | WE | On | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 18:00 | 15.1 | Sun | WE | On | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 19:00 | 14.7 | Sun | WE | Off | OFF | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 20:00 | 14.1 | Sun | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 21:00 | 13.4 | Sun | WE | Off | OFF | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 22:00 | 12.9 | Sun | WE | Off | OFF | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 23:00 | 11.7 | Sun | WE | Off | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
Mon, 10/Oct | 24:00 | 11.7 | Mon | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 1:00 | 11.8 | Mon | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 2:00 | 11.3 | Mon | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 3:00 | 11 | Mon | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 4:00 | 10.8 | Mon | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 5:00 | 10.5 | Mon | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 6:00 | 10.4 | Mon | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 7:00 | 10.8 | Mon | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 8:00 | 11 | Mon | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 9:00 | 10.3 | Mon | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 10:00 | 11.6 | Mon | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 11:00 | 12.8 | Mon | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 12:00 | 13.4 | Mon | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 13:00 | 14.7 | Mon | School Day | On | On | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 2.0166
| 14:00 | 15.3 | Mon | School Day | On | On | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 1.8509
| 15:00 | 15.8 | Mon | School Day | On | On | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 1.7127
| 16:00 | 16.9 | Mon | School Day | On | On | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 1.4089
| 17:00 | 16.7 | Mon | School Day | On | On | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 1.4641
| 18:00 | 16.6 | Mon | School Day | On | On | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 1.4917
| 19:00 | 15.7 | Mon | School Day | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 20:00 | 15.3 | Mon | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 21:00 | 15 | Mon | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 22:00 | 14.7 | Mon | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 23:00 | 13.4 | Mon | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
Tue, 11/Oct | 24:00 | 12.4 | Tue | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 1:00 | 12.9 | Tue | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 2:00 | 11.6 | Tue | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 3:00 | 12.1 | Tue | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 4:00 | 12.1 | Tue | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 5:00 | 12.9 | Tue | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 6:00 | 13 | Tue | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 7:00 | 13.4 | Tue | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 8:00 | 13.3 | Tue | School Day | On | On | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 2.4033
| 9:00 | 13.2 | Tue | School Day | On | On | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 2.431
| 10:00 | 13.2 | Tue | School Day | On | On | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 2.431
| 11:00 | 13.9 | Tue | School Day | On | On | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 2.2376
| 12:00 | 15.6 | Tue | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 13:00 | 16.9 | Tue | School Day | On | On | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 1.4089
| 14:00 | 17.4 | Tue | School Day | On | On | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 1.2707
| 15:00 | 16.8 | Tue | School Day | On | On | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 1.4365
| 16:00 | 17.1 | Tue | School Day | On | On | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 1.3536
| 17:00 | 17.3 | Tue | School Day | On | On | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 1.2984
| 18:00 | 17.1 | Tue | School Day | On | On | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 1.3536
| 19:00 | 16.1 | Tue | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 20:00 | 15.4 | Tue | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 21:00 | 14.6 | Tue | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 22:00 | 15 | Tue | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 23:00 | 14.2 | Tue | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
Wed, 12/Oct | 24:00 | 14.3 | Wed | School Day | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 1:00 | 14.1 | Wed | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 2:00 | 14 | Wed | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 3:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 4:00 | 14 | Wed | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 5:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 6:00 | 14 | Wed | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 7:00 | 13.9 | Wed | School Day | On | On | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 2.2376
| 8:00 | 13.1 | Wed | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 9:00 | 12.9 | Wed | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 10:00 | 13 | Wed | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 11:00 | 14 | Wed | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 12:00 | 17.1 | Wed | School Day | On | On | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 1.3536
| 13:00 | 18.8 | Wed | School Day | On | On | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0.88399
| 14:00 | 19.1 | Wed | School Day | On | On | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0.80112
| 15:00 | 20.3 | Wed | School Day | On | On | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0.46962
| 16:00 | 18.7 | Wed | School Day | On | On | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0.91161
| 17:00 | 18.7 | Wed | School Day | On | On | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0.91161
| 18:00 | 18.1 | Wed | School Day | On | On | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 1.0774
| 19:00 | 17.6 | Wed | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 20:00 | 17.1 | Wed | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 21:00 | 16.8 | Wed | School Day | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 22:00 | 16.7 | Wed | School Day | Off | Off | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 23:00 | 16.3 | Wed | School Day | Off | Off | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
Thu, 13/Oct | 24:00 | 16.5 | Thu | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 1:00 | 15.5 | Thu | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 2:00 | 15.6 | Thu | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 3:00 | 15.1 | Thu | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 4:00 | 15.7 | Thu | School Day | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 5:00 | 15.5 | Thu | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 6:00 | 15.4 | Thu | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 7:00 | 15.2 | Thu | School Day | On | On | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 1.8785
| 8:00 | 15.1 | Thu | School Day | On | On | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 1.9061
| 9:00 | 14.8 | Thu | School Day | On | On | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 1.989
| 10:00 | 15.4 | Thu | School Day | On | On | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 1.8232
| 11:00 | 15.4 | Thu | School Day | On | On | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 1.8232
| 12:00 | 15.9 | Thu | School Day | On | On | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 1.6851
| 13:00 | 12.9 | Thu | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 14:00 | 13.5 | Thu | School Day | On | On | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 2.3481
| 15:00 | 14.5 | Thu | School Day | On | On | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 2.0719
| 16:00 | 14.7 | Thu | School Day | On | On | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 2.0166
| 17:00 | 16.4 | Thu | School Day | On | On | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 1.547
| 18:00 | 15.2 | Thu | School Day | On | On | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 1.8785
| 19:00 | 14.2 | Thu | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 20:00 | 12.4 | Thu | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 21:00 | 12.1 | Thu | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 22:00 | 11.5 | Thu | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 23:00 | 10.9 | Thu | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
Fri, 14/Oct | 24:00 | 10.4 | Fri | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 1:00 | 9.9 | Fri | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 2:00 | 9.8 | Fri | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 3:00 | 10.1 | Fri | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 4:00 | 10.9 | Fri | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 5:00 | 10.9 | Fri | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 6:00 | 10.5 | Fri | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 7:00 | 10.2 | Fri | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 8:00 | 10 | Fri | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 9:00 | 9.9 | Fri | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 10:00 | 11.3 | Fri | School Day | On | On | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 2.9558
| 11:00 | 12.8 | Fri | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 12:00 | 14.2 | Fri | School Day | On | On | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 2.1547
| 13:00 | 14.5 | Fri | School Day | On | On | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 2.0719
| 14:00 | 14.3 | Fri | School Day | On | On | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 2.1271
| 15:00 | 15.1 | Fri | School Day | On | On | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 1.9061
| 16:00 | 15.7 | Fri | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 17:00 | 14.7 | Fri | School Day | On | On | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 2.0166
| 18:00 | 14.5 | Fri | School Day | On | On | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 2.0719
| 19:00 | 14.1 | Fri | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 20:00 | 13 | Fri | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 21:00 | 10.2 | Fri | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 22:00 | 9.1 | Fri | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 23:00 | 8.6 | Fri | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
Sat, 15/Oct | 24:00 | 8.3 | Sat | WE | Off | OFF | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 1:00 | 9.4 | Sat | WE | Off | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 2:00 | 8.7 | Sat | WE | Off | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 3:00 | 6.3 | Sat | WE | Off | OFF | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 4:00 | 7.4 | Sat | WE | Off | OFF | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 5:00 | 6.9 | Sat | WE | Off | OFF | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 6:00 | 7 | Sat | WE | Off | OFF | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 7:00 | 6.3 | Sat | WE | On | OFF | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 8:00 | 7 | Sat | WE | On | OFF | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 9:00 | 6.1 | Sat | WE | On | OFF | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 10:00 | 8.4 | Sat | WE | On | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 11:00 | 9.8 | Sat | WE | On | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 12:00 | 10.8 | Sat | WE | On | OFF | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 13:00 | 12.8 | Sat | WE | On | OFF | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 14:00 | 15.7 | Sat | WE | On | OFF | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 15:00 | 16.9 | Sat | WE | On | OFF | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 16:00 | 18 | Sat | WE | On | OFF | 22 | 21.6 | 0.4 | 1.7 | 0.76404 | 0.25 | 1035 | 0.34095 | 0
| 17:00 | 16.4 | Sat | WE | On | OFF | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 18:00 | 16.1 | Sat | WE | On | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 19:00 | 16.2 | Sat | WE | Off | OFF | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 20:00 | 15.9 | Sat | WE | Off | OFF | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 21:00 | 14.9 | Sat | WE | Off | OFF | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 22:00 | 14.2 | Sat | WE | Off | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 23:00 | 13.4 | Sat | WE | Off | OFF | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
Sun, 16/Oct | 24:00 | 13.3 | Sun | WE | Off | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 1:00 | 13.3 | Sun | WE | Off | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 2:00 | 13.7 | Sun | WE | Off | OFF | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 3:00 | 13.3 | Sun | WE | Off | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 4:00 | 13 | Sun | WE | Off | OFF | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 5:00 | 12.4 | Sun | WE | Off | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 6:00 | 12 | Sun | WE | Off | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 7:00 | 11.6 | Sun | WE | On | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 8:00 | 12 | Sun | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 9:00 | 12.3 | Sun | WE | On | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 10:00 | 13.1 | Sun | WE | On | OFF | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 11:00 | 14.2 | Sun | WE | On | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 12:00 | 16.1 | Sun | WE | On | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 13:00 | 17 | Sun | WE | On | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 14:00 | 17.9 | Sun | WE | On | OFF | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 15:00 | 18.5 | Sun | WE | On | OFF | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 16:00 | 18.3 | Sun | WE | On | OFF | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 17:00 | 18.3 | Sun | WE | On | OFF | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 18:00 | 18.1 | Sun | WE | On | OFF | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 0
| 19:00 | 17.4 | Sun | WE | Off | OFF | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 20:00 | 16.9 | Sun | WE | Off | OFF | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 21:00 | 16.6 | Sun | WE | Off | OFF | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 22:00 | 16 | Sun | WE | Off | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 23:00 | 15.1 | Sun | WE | Off | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
Mon, 17/Oct | 24:00 | 14.8 | Mon | School Day | Off | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 1:00 | 12.9 | Mon | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 2:00 | 12 | Mon | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 3:00 | 10.2 | Mon | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 4:00 | 10.4 | Mon | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 5:00 | 10.3 | Mon | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 6:00 | 9.3 | Mon | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 7:00 | 9.2 | Mon | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 8:00 | 9.1 | Mon | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 9:00 | 9.1 | Mon | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 10:00 | 10.9 | Mon | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 11:00 | 13.6 | Mon | School Day | On | On | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 2.3205
| 12:00 | 16.2 | Mon | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 13:00 | 18.6 | Mon | School Day | On | On | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0.93924
| 14:00 | 20.4 | Mon | School Day | On | On | 22 | 21.84 | 0.16 | 1.7 | 0.30562 | 0.25 | 1035 | 0.13638 | 0.44199
| 15:00 | 20.5 | Mon | School Day | On | On | 22 | 21.85 | 0.15 | 1.7 | 0.28652 | 0.25 | 1035 | 0.12785 | 0.41437
| 16:00 | 20.9 | Mon | School Day | On | On | 22 | 21.89 | 0.11 | 1.7 | 0.21011 | 0.25 | 1035 | 0.09376 | 0.30387
| 17:00 | 21.1 | Mon | School Day | On | On | 22 | 21.91 | 0.09 | 1.7 | 0.17191 | 0.25 | 1035 | 0.076713 | 0.24862
| 18:00 | 20.3 | Mon | School Day | On | On | 22 | 21.83 | 0.17 | 1.7 | 0.32472 | 0.25 | 1035 | 0.1449 | 0.46962
| 19:00 | 18.9 | Mon | School Day | Off | Off | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 20:00 | 17.2 | Mon | School Day | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 21:00 | 16.1 | Mon | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 22:00 | 14.5 | Mon | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 23:00 | 13.4 | Mon | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
Tue, 18/Oct | 24:00 | 12.3 | Tue | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 1:00 | 11.3 | Tue | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 2:00 | 10.1 | Tue | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 3:00 | 9.5 | Tue | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 4:00 | 8.6 | Tue | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 5:00 | 8.9 | Tue | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 6:00 | 7.9 | Tue | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 7:00 | 9.1 | Tue | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 8:00 | 9.4 | Tue | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 9:00 | 9.9 | Tue | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 10:00 | 10.8 | Tue | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 11:00 | 13.5 | Tue | School Day | On | On | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 2.3481
| 12:00 | 15.7 | Tue | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 13:00 | 17.4 | Tue | School Day | On | On | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 1.2707
| 14:00 | 17.7 | Tue | School Day | On | On | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 1.1879
| 15:00 | 17.6 | Tue | School Day | On | On | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 1.2155
| 16:00 | 17.8 | Tue | School Day | On | On | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 1.1602
| 17:00 | 18.6 | Tue | School Day | On | On | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0.93924
| 18:00 | 18.1 | Tue | School Day | On | On | 22 | 21.61 | 0.39 | 1.7 | 0.74494 | 0.25 | 1035 | 0.33242 | 1.0774
| 19:00 | 17.4 | Tue | School Day | Off | Off | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 20:00 | 16.6 | Tue | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 21:00 | 15.6 | Tue | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 22:00 | 15.7 | Tue | School Day | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 23:00 | 15.2 | Tue | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
Wed, 19/Oct | 24:00 | 15.4 | Wed | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 1:00 | 15.2 | Wed | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 2:00 | 15.2 | Wed | School Day | Off | Off | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 0
| 3:00 | 15.1 | Wed | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 4:00 | 14.9 | Wed | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 5:00 | 14.5 | Wed | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 6:00 | 15.1 | Wed | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 7:00 | 15 | Wed | School Day | On | On | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 1.9337
| 8:00 | 14.4 | Wed | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 9:00 | 14.4 | Wed | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 10:00 | 15 | Wed | School Day | On | On | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 1.9337
| 11:00 | 15.7 | Wed | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 12:00 | 16.7 | Wed | School Day | On | On | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 1.4641
| 13:00 | 17.5 | Wed | School Day | On | On | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 1.2431
| 14:00 | 19.2 | Wed | School Day | On | On | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0.77349
| 15:00 | 19.2 | Wed | School Day | On | On | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0.77349
| 16:00 | 19.2 | Wed | School Day | On | On | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0.77349
| 17:00 | 18.7 | Wed | School Day | On | On | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0.91161
| 18:00 | 17.6 | Wed | School Day | On | On | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 1.2155
| 19:00 | 17 | Wed | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 20:00 | 17.3 | Wed | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 21:00 | 16.9 | Wed | School Day | Off | Off | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 22:00 | 16.6 | Wed | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 23:00 | 16 | Wed | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
Thu, 20/Oct | 24:00 | 16.5 | Thu | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 1:00 | 16 | Thu | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 2:00 | 15.6 | Thu | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 3:00 | 15.8 | Thu | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 4:00 | 14.9 | Thu | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 5:00 | 14.5 | Thu | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 6:00 | 14.1 | Thu | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 7:00 | 12.8 | Thu | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 8:00 | 12 | Thu | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 9:00 | 11.4 | Thu | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 10:00 | 12.1 | Thu | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 11:00 | 13 | Thu | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 12:00 | 14.1 | Thu | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 13:00 | 15.4 | Thu | School Day | On | On | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 1.8232
| 14:00 | 15.8 | Thu | School Day | On | On | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 1.7127
| 15:00 | 17.1 | Thu | School Day | On | On | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 1.3536
| 16:00 | 16.6 | Thu | School Day | On | On | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 1.4917
| 17:00 | 16.5 | Thu | School Day | On | On | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 1.5194
| 18:00 | 15.6 | Thu | School Day | On | On | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 1.768
| 19:00 | 15.4 | Thu | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 20:00 | 15.4 | Thu | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 21:00 | 14.4 | Thu | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 22:00 | 14.6 | Thu | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 23:00 | 14.4 | Thu | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
Fri, 21/Oct | 24:00 | 15.1 | Fri | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 1:00 | 16 | Fri | School Day | Off | Off | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 2:00 | 17 | Fri | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 3:00 | 16.5 | Fri | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 4:00 | 16.8 | Fri | School Day | Off | Off | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 5:00 | 16.6 | Fri | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 6:00 | 17.1 | Fri | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 7:00 | 18.6 | Fri | School Day | On | On | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0.93924
| 8:00 | 17.8 | Fri | School Day | On | On | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 1.1602
| 9:00 | 18.2 | Fri | School Day | On | On | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 1.0497
| 10:00 | 17.5 | Fri | School Day | On | On | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 1.2431
| 11:00 | 17.8 | Fri | School Day | On | On | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 1.1602
| 12:00 | 18.2 | Fri | School Day | On | On | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 1.0497
| 13:00 | 17.8 | Fri | School Day | On | On | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 1.1602
| 14:00 | 19.4 | Fri | School Day | On | On | 22 | 21.74 | 0.26 | 1.7 | 0.49663 | 0.25 | 1035 | 0.22162 | 0.71824
| 15:00 | 19.3 | Fri | School Day | On | On | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0.74587
| 16:00 | 18.7 | Fri | School Day | On | On | 22 | 21.67 | 0.33 | 1.7 | 0.63033 | 0.25 | 1035 | 0.28128 | 0.91161
| 17:00 | 18.3 | Fri | School Day | On | On | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 1.0221
| 18:00 | 17.8 | Fri | School Day | On | On | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 1.1602
| 19:00 | 17.6 | Fri | School Day | Off | Off | 22 | 21.56 | 0.44 | 1.7 | 0.84045 | 0.25 | 1035 | 0.37504 | 0
| 20:00 | 15 | Fri | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 21:00 | 14.3 | Fri | School Day | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 22:00 | 14.4 | Fri | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 23:00 | 14.5 | Fri | School Day | Off | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
Sat, 22/Oct | 24:00 | 15.1 | Sat | WE | Off | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 1:00 | 14.2 | Sat | WE | Off | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 2:00 | 14.9 | Sat | WE | Off | OFF | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 3:00 | 13.9 | Sat | WE | Off | OFF | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 4:00 | 12.5 | Sat | WE | Off | OFF | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 5:00 | 12.9 | Sat | WE | Off | OFF | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 6:00 | 13.4 | Sat | WE | Off | OFF | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 7:00 | 13.3 | Sat | WE | On | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 8:00 | 13.4 | Sat | WE | On | OFF | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 9:00 | 16.3 | Sat | WE | On | OFF | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 10:00 | 17.2 | Sat | WE | On | OFF | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 11:00 | 17.7 | Sat | WE | On | OFF | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 12:00 | 17.5 | Sat | WE | On | OFF | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 13:00 | 17.2 | Sat | WE | On | OFF | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 14:00 | 19 | Sat | WE | On | OFF | 22 | 21.7 | 0.3 | 1.7 | 0.57303 | 0.25 | 1035 | 0.25571 | 0
| 15:00 | 20.1 | Sat | WE | On | OFF | 22 | 21.81 | 0.19 | 1.7 | 0.36292 | 0.25 | 1035 | 0.16195 | 0
| 16:00 | 19.8 | Sat | WE | On | OFF | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 17:00 | 19.2 | Sat | WE | On | OFF | 22 | 21.72 | 0.28 | 1.7 | 0.53483 | 0.25 | 1035 | 0.23866 | 0
| 18:00 | 18.9 | Sat | WE | On | OFF | 22 | 21.69 | 0.31 | 1.7 | 0.59213 | 0.25 | 1035 | 0.26423 | 0
| 19:00 | 16.1 | Sat | WE | Off | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 20:00 | 15.6 | Sat | WE | Off | OFF | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 21:00 | 15.8 | Sat | WE | Off | OFF | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 22:00 | 15.4 | Sat | WE | Off | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 23:00 | 14.9 | Sat | WE | Off | OFF | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
Sun, 23/Oct | 24:00 | 14.1 | Sun | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 1:00 | 14.1 | Sun | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 2:00 | 13.8 | Sun | WE | Off | OFF | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 3:00 | 14.1 | Sun | WE | Off | OFF | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 4:00 | 14.6 | Sun | WE | Off | OFF | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 5:00 | 14 | Sun | WE | Off | OFF | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 6:00 | 13.1 | Sun | WE | Off | OFF | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 7:00 | 13.3 | Sun | WE | On | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 8:00 | 13.6 | Sun | WE | On | OFF | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 9:00 | 13.3 | Sun | WE | On | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 10:00 | 14.8 | Sun | WE | On | OFF | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 11:00 | 15.4 | Sun | WE | On | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 12:00 | 15.9 | Sun | WE | On | OFF | 22 | 21.39 | 0.61 | 1.7 | 1.1652 | 0.25 | 1035 | 0.51994 | 0
| 13:00 | 16.6 | Sun | WE | On | OFF | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 14:00 | 17.4 | Sun | WE | On | OFF | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 0
| 15:00 | 17.3 | Sun | WE | On | OFF | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 16:00 | 17.5 | Sun | WE | On | OFF | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 17:00 | 17.5 | Sun | WE | On | OFF | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 0
| 18:00 | 16.9 | Sun | WE | On | OFF | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 19:00 | 16.2 | Sun | WE | Off | OFF | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 20:00 | 16 | Sun | WE | Off | OFF | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 0
| 21:00 | 15.6 | Sun | WE | Off | OFF | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 22:00 | 15.5 | Sun | WE | Off | OFF | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 23:00 | 15.4 | Sun | WE | Off | OFF | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
Mon, 24/Oct | 24:00 | 14.9 | Mon | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 1:00 | 13.3 | Mon | School Day | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 2:00 | 12.5 | Mon | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 3:00 | 11.2 | Mon | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 4:00 | 10.9 | Mon | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 5:00 | 9.9 | Mon | School Day | Off | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 6:00 | 9.4 | Mon | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 7:00 | 9.8 | Mon | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 8:00 | 9.3 | Mon | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 9:00 | 9.1 | Mon | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 10:00 | 9.5 | Mon | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 11:00 | 11.3 | Mon | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 12:00 | 13.2 | Mon | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 13:00 | 15 | Mon | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 14:00 | 15.5 | Mon | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 15:00 | 16.2 | Mon | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 16:00 | 16.5 | Mon | School Day | Off | Off | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 17:00 | 16.4 | Mon | School Day | Off | Off | 22 | 21.44 | 0.56 | 1.7 | 1.0697 | 0.25 | 1035 | 0.47732 | 0
| 18:00 | 15.6 | Mon | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 19:00 | 14.4 | Mon | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 20:00 | 13.7 | Mon | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 21:00 | 13.1 | Mon | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 22:00 | 12.7 | Mon | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 23:00 | 11.9 | Mon | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
Tue, 25/Oct | 24:00 | 11.5 | Tue | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 1:00 | 11.4 | Tue | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 2:00 | 11.6 | Tue | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 3:00 | 12.3 | Tue | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 4:00 | 12.8 | Tue | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 5:00 | 12.9 | Tue | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 6:00 | 13.1 | Tue | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 7:00 | 13 | Tue | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 8:00 | 12.9 | Tue | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 9:00 | 13.1 | Tue | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 10:00 | 13.5 | Tue | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 11:00 | 14.8 | Tue | School Day | Off | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 12:00 | 17.1 | Tue | School Day | Off | Off | 22 | 21.51 | 0.49 | 1.7 | 0.93595 | 0.25 | 1035 | 0.41766 | 0
| 13:00 | 17.7 | Tue | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 14:00 | 18.2 | Tue | School Day | Off | Off | 22 | 21.62 | 0.38 | 1.7 | 0.72584 | 0.25 | 1035 | 0.3239 | 0
| 15:00 | 19.1 | Tue | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 16:00 | 19.1 | Tue | School Day | Off | Off | 22 | 21.71 | 0.29 | 1.7 | 0.55393 | 0.25 | 1035 | 0.24719 | 0
| 17:00 | 18.5 | Tue | School Day | Off | Off | 22 | 21.65 | 0.35 | 1.7 | 0.66854 | 0.25 | 1035 | 0.29833 | 0
| 18:00 | 17.7 | Tue | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 19:00 | 15.7 | Tue | School Day | Off | Off | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 20:00 | 14.6 | Tue | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 21:00 | 13.4 | Tue | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 22:00 | 13 | Tue | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 23:00 | 12.5 | Tue | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
Wed, 26/Oct | 24:00 | 13.2 | Wed | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 1:00 | 12.8 | Wed | School Day | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 2:00 | 12.1 | Wed | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 3:00 | 12.4 | Wed | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 4:00 | 12.9 | Wed | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 5:00 | 13.4 | Wed | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 6:00 | 13.7 | Wed | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 7:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 8:00 | 14 | Wed | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 9:00 | 14.6 | Wed | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 10:00 | 14.7 | Wed | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 11:00 | 14.9 | Wed | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 12:00 | 14.6 | Wed | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 13:00 | 14.7 | Wed | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 14:00 | 14.7 | Wed | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 15:00 | 14.7 | Wed | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 16:00 | 14.7 | Wed | School Day | Off | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 17:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 18:00 | 13.6 | Wed | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 19:00 | 13.7 | Wed | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 20:00 | 13.5 | Wed | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 21:00 | 13.4 | Wed | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 22:00 | 12.7 | Wed | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 23:00 | 12.5 | Wed | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
Thu, 27/Oct | 24:00 | 12.5 | Thu | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 1:00 | 12.6 | Thu | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 2:00 | 12.4 | Thu | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 3:00 | 12.4 | Thu | School Day | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 4:00 | 12.7 | Thu | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 5:00 | 13 | Thu | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 6:00 | 13.6 | Thu | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 7:00 | 15 | Thu | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 8:00 | 15.1 | Thu | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 9:00 | 15.1 | Thu | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 10:00 | 15.3 | Thu | School Day | Off | Off | 22 | 21.33 | 0.67 | 1.7 | 1.2798 | 0.25 | 1035 | 0.57108 | 0
| 11:00 | 15.8 | Thu | School Day | Off | Off | 22 | 21.38 | 0.62 | 1.7 | 1.1843 | 0.25 | 1035 | 0.52847 | 0
| 12:00 | 16.2 | Thu | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 13:00 | 17.3 | Thu | School Day | Off | Off | 22 | 21.53 | 0.47 | 1.7 | 0.89775 | 0.25 | 1035 | 0.40061 | 0
| 14:00 | 18.4 | Thu | School Day | Off | Off | 22 | 21.64 | 0.36 | 1.7 | 0.68764 | 0.25 | 1035 | 0.30685 | 0
| 15:00 | 19.8 | Thu | School Day | Off | Off | 22 | 21.78 | 0.22 | 1.7 | 0.42022 | 0.25 | 1035 | 0.18752 | 0
| 16:00 | 19.3 | Thu | School Day | Off | Off | 22 | 21.73 | 0.27 | 1.7 | 0.51573 | 0.25 | 1035 | 0.23014 | 0
| 17:00 | 18.6 | Thu | School Day | Off | Off | 22 | 21.66 | 0.34 | 1.7 | 0.64944 | 0.25 | 1035 | 0.2898 | 0
| 18:00 | 17.9 | Thu | School Day | Off | Off | 22 | 21.59 | 0.41 | 1.7 | 0.78314 | 0.25 | 1035 | 0.34947 | 0
| 19:00 | 17 | Thu | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 20:00 | 17.2 | Thu | School Day | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 21:00 | 15 | Thu | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 22:00 | 16.6 | Thu | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 23:00 | 16.1 | Thu | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
Fri, 28/Oct | 24:00 | 16.2 | Fri | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 1:00 | 16.6 | Fri | School Day | Off | Off | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 2:00 | 17.2 | Fri | School Day | Off | Off | 22 | 21.52 | 0.48 | 1.7 | 0.91685 | 0.25 | 1035 | 0.40914 | 0
| 3:00 | 16.1 | Fri | School Day | Off | Off | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 4:00 | 17 | Fri | School Day | Off | Off | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 5:00 | 17.7 | Fri | School Day | Off | Off | 22 | 21.57 | 0.43 | 1.7 | 0.82134 | 0.25 | 1035 | 0.36652 | 0
| 6:00 | 18.3 | Fri | School Day | Off | Off | 22 | 21.63 | 0.37 | 1.7 | 0.70674 | 0.25 | 1035 | 0.31538 | 0
| 7:00 | 16.2 | Fri | School Day | Off | Off | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 8:00 | 15.5 | Fri | School Day | Off | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 9:00 | 15 | Fri | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 10:00 | 14.4 | Fri | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 11:00 | 14.4 | Fri | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 12:00 | 14.9 | Fri | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 13:00 | 15.6 | Fri | School Day | Off | Off | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 14:00 | 14.4 | Fri | School Day | Off | Off | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 0
| 15:00 | 12.3 | Fri | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 16:00 | 14.2 | Fri | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 17:00 | 13.8 | Fri | School Day | Off | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 18:00 | 13.7 | Fri | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 19:00 | 13 | Fri | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 20:00 | 13.3 | Fri | School Day | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 21:00 | 13.5 | Fri | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 22:00 | 13.4 | Fri | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 23:00 | 13.1 | Fri | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
Sat, 29/Oct | 24:00 | 13.3 | Sat | WE | Off | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 1:00 | 12.9 | Sat | WE | Off | OFF | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 2:00 | 12.3 | Sat | WE | Off | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 3:00 | 12.3 | Sat | WE | Off | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 4:00 | 12.1 | Sat | WE | Off | OFF | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 5:00 | 12 | Sat | WE | Off | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 6:00 | 12 | Sat | WE | Off | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 7:00 | 12 | Sat | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 8:00 | 12 | Sat | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 9:00 | 12 | Sat | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 10:00 | 11.7 | Sat | WE | On | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 11:00 | 11.9 | Sat | WE | On | OFF | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 12:00 | 13.5 | Sat | WE | On | OFF | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 13:00 | 14.6 | Sat | WE | On | OFF | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 14:00 | 15.6 | Sat | WE | On | OFF | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 15:00 | 14.6 | Sat | WE | On | OFF | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 16:00 | 14.6 | Sat | WE | On | OFF | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 17:00 | 12 | Sat | WE | On | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 18:00 | 11.3 | Sat | WE | On | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 19:00 | 11.7 | Sat | WE | Off | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 20:00 | 13.8 | Sat | WE | Off | OFF | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 21:00 | 16.2 | Sat | WE | Off | OFF | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 22:00 | 16.9 | Sat | WE | Off | OFF | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 23:00 | 17 | Sat | WE | Off | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
Sun, 30/Oct | 24:00 | 16.9 | Sun | WE | Off | OFF | 22 | 21.49 | 0.51 | 1.7 | 0.97415 | 0.25 | 1035 | 0.43471 | 0
| 1:00 | 16.8 | Sun | WE | Off | OFF | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 2:00 | 16.7 | Sun | WE | Off | OFF | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 3:00 | 16.8 | Sun | WE | Off | OFF | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 0
| 4:00 | 16.6 | Sun | WE | Off | OFF | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 5:00 | 16.6 | Sun | WE | Off | OFF | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 0
| 6:00 | 16.7 | Sun | WE | Off | OFF | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 0
| 7:00 | 16.2 | Sun | WE | On | OFF | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 0
| 8:00 | 14.9 | Sun | WE | On | OFF | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 9:00 | 14.2 | Sun | WE | On | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 10:00 | 14.2 | Sun | WE | On | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 11:00 | 14.3 | Sun | WE | On | OFF | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 12:00 | 14.2 | Sun | WE | On | OFF | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 13:00 | 14.8 | Sun | WE | On | OFF | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 14:00 | 15.6 | Sun | WE | On | OFF | 22 | 21.36 | 0.64 | 1.7 | 1.2225 | 0.25 | 1035 | 0.54551 | 0
| 15:00 | 16.1 | Sun | WE | On | OFF | 22 | 21.41 | 0.59 | 1.7 | 1.127 | 0.25 | 1035 | 0.5029 | 0
| 16:00 | 16.3 | Sun | WE | On | OFF | 22 | 21.43 | 0.57 | 1.7 | 1.0888 | 0.25 | 1035 | 0.48585 | 0
| 17:00 | 15.5 | Sun | WE | On | OFF | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 18:00 | 15 | Sun | WE | On | OFF | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 19:00 | 13 | Sun | WE | Off | OFF | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 20:00 | 14 | Sun | WE | Off | OFF | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 21:00 | 14.3 | Sun | WE | Off | OFF | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
| 22:00 | 11.8 | Sun | WE | Off | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 23:00 | 13.9 | Sun | WE | Off | OFF | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
Mon, 31/Oct | 24:00 | 13.6 | Mon | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 1:00 | 13.4 | Mon | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 2:00 | 12.5 | Mon | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 3:00 | 12.5 | Mon | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 4:00 | 12.6 | Mon | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 5:00 | 12.6 | Mon | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 6:00 | 13.1 | Mon | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 7:00 | 13.6 | Mon | School Day | On | On | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 2.3205
| 8:00 | 13.7 | Mon | School Day | On | On | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 2.2928
| 9:00 | 13.8 | Mon | School Day | On | On | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 2.2652
| 10:00 | 14.3 | Mon | School Day | On | On | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 2.1271
| 11:00 | 15.5 | Mon | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 12:00 | 17 | Mon | School Day | On | On | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 1.3812
| 13:00 | 17.5 | Mon | School Day | On | On | 22 | 21.55 | 0.45 | 1.7 | 0.85955 | 0.25 | 1035 | 0.38356 | 1.2431
| 14:00 | 16.7 | Mon | School Day | On | On | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 1.4641
| 15:00 | 17.8 | Mon | School Day | On | On | 22 | 21.58 | 0.42 | 1.7 | 0.80224 | 0.25 | 1035 | 0.35799 | 1.1602
| 16:00 | 18.8 | Mon | School Day | On | On | 22 | 21.68 | 0.32 | 1.7 | 0.61123 | 0.25 | 1035 | 0.27276 | 0.88399
| 17:00 | 17.4 | Mon | School Day | On | On | 22 | 21.54 | 0.46 | 1.7 | 0.87865 | 0.25 | 1035 | 0.39209 | 1.2707
| 18:00 | 16.2 | Mon | School Day | On | On | 22 | 21.42 | 0.58 | 1.7 | 1.1079 | 0.25 | 1035 | 0.49437 | 1.6022
| 19:00 | 13.6 | Mon | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 20:00 | 12.3 | Mon | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 21:00 | 11.9 | Mon | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 22:00 | 11.8 | Mon | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 23:00 | 11 | Mon | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
Tue, 01/Nov | 24:00 | 10 | Tue | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 1:00 | 10.2 | Tue | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 2:00 | 9.8 | Tue | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 3:00 | 9.7 | Tue | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 4:00 | 9.4 | Tue | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 5:00 | 9.2 | Tue | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 6:00 | 9.4 | Tue | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 7:00 | 9.5 | Tue | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 8:00 | 9 | Tue | School Day | On | On | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 3.5912
| 9:00 | 10.5 | Tue | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 10:00 | 11.1 | Tue | School Day | On | On | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 3.0111
| 11:00 | 12.2 | Tue | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 12:00 | 13.4 | Tue | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 13:00 | 14.3 | Tue | School Day | On | On | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 2.1271
| 14:00 | 14.9 | Tue | School Day | On | On | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 1.9614
| 15:00 | 15.1 | Tue | School Day | On | On | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 1.9061
| 16:00 | 15.5 | Tue | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 17:00 | 14.6 | Tue | School Day | On | On | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 2.0442
| 18:00 | 14.3 | Tue | School Day | On | On | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 2.1271
| 19:00 | 12.9 | Tue | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 20:00 | 13.3 | Tue | School Day | Off | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 21:00 | 12.7 | Tue | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 22:00 | 12 | Tue | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 23:00 | 11.6 | Tue | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
Wed, 02/Nov | 24:00 | 11.8 | Wed | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 1:00 | 11.6 | Wed | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 2:00 | 11.1 | Wed | School Day | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 3:00 | 10.1 | Wed | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 4:00 | 12.1 | Wed | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 5:00 | 13.2 | Wed | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 6:00 | 13.6 | Wed | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 7:00 | 13.3 | Wed | School Day | On | On | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 2.4033
| 8:00 | 14 | Wed | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 9:00 | 13.9 | Wed | School Day | On | On | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 2.2376
| 10:00 | 14.5 | Wed | School Day | On | On | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 2.0719
| 11:00 | 14.7 | Wed | School Day | On | On | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 2.0166
| 12:00 | 15.4 | Wed | School Day | On | On | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 1.8232
| 13:00 | 11.8 | Wed | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 14:00 | 11.6 | Wed | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 15:00 | 11.6 | Wed | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 16:00 | 11.6 | Wed | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 17:00 | 11.5 | Wed | School Day | On | On | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 2.9006
| 18:00 | 11.7 | Wed | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 19:00 | 11.8 | Wed | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 20:00 | 10 | Wed | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 21:00 | 10 | Wed | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 22:00 | 10.4 | Wed | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 23:00 | 9.6 | Wed | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
Thu, 03/Nov | 24:00 | 9.3 | Thu | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 1:00 | 8.9 | Thu | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 2:00 | 8.6 | Thu | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 3:00 | 8.6 | Thu | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 4:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 5:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 6:00 | 7.1 | Thu | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 7:00 | 7.1 | Thu | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 8:00 | 7.1 | Thu | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 9:00 | 8.1 | Thu | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 10:00 | 9.7 | Thu | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 11:00 | 11.8 | Thu | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 12:00 | 13.4 | Thu | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 13:00 | 13.8 | Thu | School Day | On | On | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 2.2652
| 14:00 | 14.5 | Thu | School Day | On | On | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 2.0719
| 15:00 | 14.1 | Thu | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 16:00 | 13.6 | Thu | School Day | On | On | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 2.3205
| 17:00 | 12.7 | Thu | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 18:00 | 13 | Thu | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 19:00 | 11.9 | Thu | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 20:00 | 11 | Thu | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 21:00 | 9.6 | Thu | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 22:00 | 8.5 | Thu | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 23:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
Fri, 04/Nov | 24:00 | 7.3 | Fri | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 1:00 | 7.2 | Fri | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 2:00 | 7.4 | Fri | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 3:00 | 7.5 | Fri | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 4:00 | 8 | Fri | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 5:00 | 8.8 | Fri | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 6:00 | 9.7 | Fri | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 7:00 | 10.5 | Fri | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 8:00 | 11.6 | Fri | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 9:00 | 12.1 | Fri | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 10:00 | 12.7 | Fri | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 11:00 | 12.1 | Fri | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 12:00 | 12.2 | Fri | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 13:00 | 12.9 | Fri | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 14:00 | 13.1 | Fri | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 15:00 | 12.5 | Fri | School Day | On | On | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 2.6243
| 16:00 | 12.2 | Fri | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 17:00 | 11.6 | Fri | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 18:00 | 10.1 | Fri | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 19:00 | 9.3 | Fri | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 20:00 | 8.3 | Fri | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 21:00 | 7 | Fri | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 22:00 | 6.2 | Fri | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 23:00 | 6 | Fri | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
Sat, 05/Nov | 24:00 | 5.5 | Sat | WE | Off | OFF | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 1:00 | 5.3 | Sat | WE | Off | OFF | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 2:00 | 5.2 | Sat | WE | Off | OFF | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 3:00 | 4.6 | Sat | WE | Off | OFF | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 4:00 | 4.3 | Sat | WE | Off | OFF | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 5:00 | 3.8 | Sat | WE | Off | OFF | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 6:00 | 3.6 | Sat | WE | Off | OFF | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 7:00 | 3.7 | Sat | WE | On | OFF | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 8:00 | 3.7 | Sat | WE | On | OFF | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 9:00 | 4.5 | Sat | WE | On | OFF | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 10:00 | 5.6 | Sat | WE | On | OFF | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 11:00 | 6.5 | Sat | WE | On | OFF | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 12:00 | 8.7 | Sat | WE | On | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 13:00 | 10.9 | Sat | WE | On | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 14:00 | 11.1 | Sat | WE | On | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 15:00 | 11.9 | Sat | WE | On | OFF | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 16:00 | 9.2 | Sat | WE | On | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 17:00 | 8.9 | Sat | WE | On | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 18:00 | 9.1 | Sat | WE | On | OFF | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 19:00 | 9 | Sat | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 20:00 | 9.2 | Sat | WE | Off | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 21:00 | 8.9 | Sat | WE | Off | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 22:00 | 8.7 | Sat | WE | Off | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 23:00 | 8.4 | Sat | WE | Off | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
Sun, 06/Nov | 24:00 | 7.1 | Sun | WE | Off | OFF | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 1:00 | 5.9 | Sun | WE | Off | OFF | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 2:00 | 5.4 | Sun | WE | Off | OFF | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 3:00 | 4.7 | Sun | WE | Off | OFF | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 4:00 | 3.6 | Sun | WE | Off | OFF | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 5:00 | 3.5 | Sun | WE | Off | OFF | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 6:00 | 3.6 | Sun | WE | Off | OFF | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 7:00 | 3.3 | Sun | WE | On | OFF | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 8:00 | 3.1 | Sun | WE | On | OFF | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 9:00 | 2.9 | Sun | WE | On | OFF | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 10:00 | 4.8 | Sun | WE | On | OFF | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 11:00 | 6.8 | Sun | WE | On | OFF | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 12:00 | 8.2 | Sun | WE | On | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 13:00 | 9.5 | Sun | WE | On | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 14:00 | 10 | Sun | WE | On | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 15:00 | 10.7 | Sun | WE | On | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 16:00 | 11.3 | Sun | WE | On | OFF | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 17:00 | 9.7 | Sun | WE | On | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 18:00 | 8.4 | Sun | WE | On | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 19:00 | 8.2 | Sun | WE | Off | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 20:00 | 8.2 | Sun | WE | Off | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 21:00 | 7.7 | Sun | WE | Off | OFF | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 22:00 | 7.7 | Sun | WE | Off | OFF | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 23:00 | 6.9 | Sun | WE | Off | OFF | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
Mon, 07/Nov | 24:00 | 7.5 | Mon | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 1:00 | 6.1 | Mon | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 2:00 | 4.4 | Mon | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 3:00 | 4.8 | Mon | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 4:00 | 4 | Mon | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 5:00 | 5.5 | Mon | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 6:00 | 6.1 | Mon | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 7:00 | 6.8 | Mon | School Day | On | On | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 4.199
| 8:00 | 7.1 | Mon | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 9:00 | 8.1 | Mon | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 10:00 | 9.2 | Mon | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 11:00 | 10.7 | Mon | School Day | On | On | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 3.1216
| 12:00 | 11.8 | Mon | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 13:00 | 13.1 | Mon | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 14:00 | 13.1 | Mon | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 15:00 | 13.1 | Mon | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 16:00 | 13.1 | Mon | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 17:00 | 12.8 | Mon | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 18:00 | 12.5 | Mon | School Day | On | On | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 2.6243
| 19:00 | 12.1 | Mon | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 20:00 | 12.3 | Mon | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 21:00 | 12 | Mon | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 22:00 | 11.2 | Mon | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 23:00 | 10.7 | Mon | School Day | Off | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
Tue, 08/Nov | 24:00 | 10.2 | Tue | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 1:00 | 10 | Tue | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 2:00 | 9.4 | Tue | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 3:00 | 9.5 | Tue | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 4:00 | 9.3 | Tue | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 5:00 | 9.1 | Tue | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 6:00 | 9.1 | Tue | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 7:00 | 9.2 | Tue | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 8:00 | 9.2 | Tue | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 9:00 | 9.2 | Tue | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 10:00 | 10.5 | Tue | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 11:00 | 13.5 | Tue | School Day | On | On | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 2.3481
| 12:00 | 15.5 | Tue | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 13:00 | 14.3 | Tue | School Day | On | On | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 2.1271
| 14:00 | 12.7 | Tue | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 15:00 | 9.7 | Tue | School Day | On | On | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 3.3978
| 16:00 | 8.3 | Tue | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 17:00 | 7 | Tue | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 18:00 | 8.6 | Tue | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 19:00 | 9.1 | Tue | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 20:00 | 8.8 | Tue | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 21:00 | 8.6 | Tue | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 22:00 | 8.4 | Tue | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 23:00 | 7.7 | Tue | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
Wed, 09/Nov | 24:00 | 7.6 | Wed | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 1:00 | 7 | Wed | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 2:00 | 6.5 | Wed | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 3:00 | 6.5 | Wed | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 4:00 | 6 | Wed | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 5:00 | 5.9 | Wed | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 6:00 | 6 | Wed | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 7:00 | 4.9 | Wed | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 8:00 | 4.5 | Wed | School Day | On | On | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 4.8343
| 9:00 | 5.9 | Wed | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 10:00 | 7.1 | Wed | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 11:00 | 8.4 | Wed | School Day | On | On | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 3.757
| 12:00 | 10.4 | Wed | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 13:00 | 11 | Wed | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 14:00 | 12.3 | Wed | School Day | On | On | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 2.6796
| 15:00 | 12.6 | Wed | School Day | On | On | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 2.5967
| 16:00 | 12 | Wed | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 17:00 | 11.8 | Wed | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 18:00 | 11.4 | Wed | School Day | On | On | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 2.9282
| 19:00 | 11.4 | Wed | School Day | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 20:00 | 11.7 | Wed | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 21:00 | 11.9 | Wed | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 22:00 | 11.9 | Wed | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 23:00 | 12.1 | Wed | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
Thu, 10/Nov | 24:00 | 11.6 | Thu | School Day | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 1:00 | 10.8 | Thu | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 2:00 | 10.4 | Thu | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 3:00 | 10.9 | Thu | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 4:00 | 11.7 | Thu | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 5:00 | 11.2 | Thu | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 6:00 | 11.2 | Thu | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 7:00 | 11.2 | Thu | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 8:00 | 11.6 | Thu | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 9:00 | 11.7 | Thu | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 10:00 | 12.3 | Thu | School Day | On | On | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 2.6796
| 11:00 | 13 | Thu | School Day | On | On | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 2.4862
| 12:00 | 12.8 | Thu | School Day | On | On | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 2.5415
| 13:00 | 13.5 | Thu | School Day | On | On | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 2.3481
| 14:00 | 14.2 | Thu | School Day | On | On | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 2.1547
| 15:00 | 15 | Thu | School Day | On | On | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 1.9337
| 16:00 | 15.1 | Thu | School Day | On | On | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 1.9061
| 17:00 | 15.5 | Thu | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 18:00 | 15.5 | Thu | School Day | On | On | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 1.7956
| 19:00 | 15.4 | Thu | School Day | Off | Off | 22 | 21.34 | 0.66 | 1.7 | 1.2607 | 0.25 | 1035 | 0.56256 | 0
| 20:00 | 15.1 | Thu | School Day | Off | Off | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 21:00 | 15 | Thu | School Day | Off | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 22:00 | 14.9 | Thu | School Day | Off | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 23:00 | 14.3 | Thu | School Day | Off | Off | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 0
Fri, 11/Nov | 24:00 | 14.2 | Fri | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 1:00 | 14 | Fri | School Day | Off | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 2:00 | 13.7 | Fri | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 3:00 | 13.7 | Fri | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 4:00 | 13.6 | Fri | School Day | Off | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 5:00 | 13.5 | Fri | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 6:00 | 13.7 | Fri | School Day | Off | Off | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 0
| 7:00 | 13.7 | Fri | School Day | On | On | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 2.2928
| 8:00 | 14 | Fri | School Day | On | On | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 2.21
| 9:00 | 14.3 | Fri | School Day | On | On | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 2.1271
| 10:00 | 14.4 | Fri | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 11:00 | 14.7 | Fri | School Day | On | On | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 2.0166
| 12:00 | 15.2 | Fri | School Day | On | On | 22 | 21.32 | 0.68 | 1.7 | 1.2989 | 0.25 | 1035 | 0.57961 | 1.8785
| 13:00 | 15.7 | Fri | School Day | On | On | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 1.7404
| 14:00 | 16.6 | Fri | School Day | On | On | 22 | 21.46 | 0.54 | 1.7 | 1.0315 | 0.25 | 1035 | 0.46028 | 1.4917
| 15:00 | 16.8 | Fri | School Day | On | On | 22 | 21.48 | 0.52 | 1.7 | 0.99325 | 0.25 | 1035 | 0.44323 | 1.4365
| 16:00 | 16.7 | Fri | School Day | On | On | 22 | 21.47 | 0.53 | 1.7 | 1.0124 | 0.25 | 1035 | 0.45175 | 1.4641
| 17:00 | 16 | Fri | School Day | On | On | 22 | 21.4 | 0.6 | 1.7 | 1.1461 | 0.25 | 1035 | 0.51142 | 1.6575
| 18:00 | 14.6 | Fri | School Day | On | On | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 2.0442
| 19:00 | 13.4 | Fri | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 20:00 | 13 | Fri | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 21:00 | 13 | Fri | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 22:00 | 11.9 | Fri | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 23:00 | 12.1 | Fri | School Day | Off | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
Sat, 12/Nov | 24:00 | 10 | Sat | WE | Off | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 1:00 | 10.7 | Sat | WE | Off | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 2:00 | 10.6 | Sat | WE | Off | OFF | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 3:00 | 9.7 | Sat | WE | Off | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 4:00 | 10.3 | Sat | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 5:00 | 10.3 | Sat | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 6:00 | 9.5 | Sat | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 7:00 | 9.3 | Sat | WE | On | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 8:00 | 9.4 | Sat | WE | On | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 9:00 | 9.5 | Sat | WE | On | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 10:00 | 10.4 | Sat | WE | On | OFF | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 11:00 | 12.4 | Sat | WE | On | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 12:00 | 13.8 | Sat | WE | On | OFF | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 13:00 | 15.1 | Sat | WE | On | OFF | 22 | 21.31 | 0.69 | 1.7 | 1.318 | 0.25 | 1035 | 0.58813 | 0
| 14:00 | 16.5 | Sat | WE | On | OFF | 22 | 21.45 | 0.55 | 1.7 | 1.0506 | 0.25 | 1035 | 0.4688 | 0
| 15:00 | 17 | Sat | WE | On | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 16:00 | 17 | Sat | WE | On | OFF | 22 | 21.5 | 0.5 | 1.7 | 0.95505 | 0.25 | 1035 | 0.42618 | 0
| 17:00 | 15.7 | Sat | WE | On | OFF | 22 | 21.37 | 0.63 | 1.7 | 1.2034 | 0.25 | 1035 | 0.53699 | 0
| 18:00 | 12.7 | Sat | WE | On | OFF | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 19:00 | 13.1 | Sat | WE | Off | OFF | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 20:00 | 11.1 | Sat | WE | Off | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 21:00 | 10.6 | Sat | WE | Off | OFF | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 22:00 | 10.7 | Sat | WE | Off | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 23:00 | 9.1 | Sat | WE | Off | OFF | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
Sun, 13/Nov | 24:00 | 9 | Sun | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 1:00 | 8.4 | Sun | WE | Off | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 2:00 | 7.7 | Sun | WE | Off | OFF | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 3:00 | 8.2 | Sun | WE | Off | OFF | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 4:00 | 7.6 | Sun | WE | Off | OFF | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 5:00 | 6.7 | Sun | WE | Off | OFF | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 6:00 | 6.5 | Sun | WE | Off | OFF | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 7:00 | 6.3 | Sun | WE | On | OFF | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 8:00 | 6.2 | Sun | WE | On | OFF | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 9:00 | 6.7 | Sun | WE | On | OFF | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 10:00 | 7.4 | Sun | WE | On | OFF | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 11:00 | 8.1 | Sun | WE | On | OFF | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 12:00 | 8.7 | Sun | WE | On | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 13:00 | 8.8 | Sun | WE | On | OFF | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 14:00 | 9.2 | Sun | WE | On | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 15:00 | 9.6 | Sun | WE | On | OFF | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 16:00 | 9.3 | Sun | WE | On | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 17:00 | 9.3 | Sun | WE | On | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 18:00 | 9.1 | Sun | WE | On | OFF | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 19:00 | 9 | Sun | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 20:00 | 9.2 | Sun | WE | Off | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 21:00 | 9.5 | Sun | WE | Off | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 22:00 | 9.6 | Sun | WE | Off | OFF | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 23:00 | 9.6 | Sun | WE | Off | OFF | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
Mon, 14/Nov | 24:00 | 9.1 | Mon | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 1:00 | 8.6 | Mon | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 2:00 | 8.1 | Mon | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 3:00 | 8 | Mon | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 4:00 | 8.1 | Mon | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 5:00 | 7.9 | Mon | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 6:00 | 7.4 | Mon | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 7:00 | 7.1 | Mon | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 8:00 | 7.3 | Mon | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 9:00 | 7.6 | Mon | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 10:00 | 7.7 | Mon | School Day | On | On | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 3.9503
| 11:00 | 8 | Mon | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 12:00 | 8.1 | Mon | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 13:00 | 8.1 | Mon | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 14:00 | 8.5 | Mon | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 15:00 | 8.6 | Mon | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 16:00 | 8.7 | Mon | School Day | On | On | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 3.6741
| 17:00 | 8.5 | Mon | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 18:00 | 8.3 | Mon | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 19:00 | 8 | Mon | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 20:00 | 8.5 | Mon | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 21:00 | 8.9 | Mon | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 22:00 | 8.5 | Mon | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 23:00 | 7.3 | Mon | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
Tue, 15/Nov | 24:00 | 7.9 | Tue | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 1:00 | 8.2 | Tue | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 2:00 | 8.5 | Tue | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 3:00 | 8.9 | Tue | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 4:00 | 8.4 | Tue | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 5:00 | 8.9 | Tue | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 6:00 | 9.2 | Tue | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 7:00 | 10 | Tue | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 8:00 | 10.8 | Tue | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 9:00 | 10.4 | Tue | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 10:00 | 10.7 | Tue | School Day | On | On | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 3.1216
| 11:00 | 11.2 | Tue | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 12:00 | 11.7 | Tue | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 13:00 | 11.8 | Tue | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 14:00 | 12.1 | Tue | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 15:00 | 12.1 | Tue | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 16:00 | 12.2 | Tue | School Day | On | On | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 2.7072
| 17:00 | 12 | Tue | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 18:00 | 11.9 | Tue | School Day | On | On | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 2.7901
| 19:00 | 12 | Tue | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 20:00 | 11.7 | Tue | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 21:00 | 11.7 | Tue | School Day | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 22:00 | 11.3 | Tue | School Day | Off | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 23:00 | 11.2 | Tue | School Day | Off | Off | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
Wed, 16/Nov | 24:00 | 10.8 | Wed | School Day | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 1:00 | 9.3 | Wed | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 2:00 | 8.8 | Wed | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 3:00 | 8.6 | Wed | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 4:00 | 6.4 | Wed | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 5:00 | 5.8 | Wed | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 6:00 | 5 | Wed | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 7:00 | 6.3 | Wed | School Day | On | On | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 4.3371
| 8:00 | 7 | Wed | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 9:00 | 7 | Wed | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 10:00 | 8.1 | Wed | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 11:00 | 9.6 | Wed | School Day | On | On | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 3.4255
| 12:00 | 10.6 | Wed | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 13:00 | 11.6 | Wed | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 14:00 | 11.8 | Wed | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 15:00 | 11.6 | Wed | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 16:00 | 10.7 | Wed | School Day | On | On | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 3.1216
| 17:00 | 9.8 | Wed | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 18:00 | 9.2 | Wed | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 19:00 | 8 | Wed | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 20:00 | 7.3 | Wed | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 21:00 | 7.1 | Wed | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 22:00 | 7.1 | Wed | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 23:00 | 6.5 | Wed | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
Thu, 17/Nov | 24:00 | 5.6 | Thu | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 1:00 | 5.9 | Thu | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 2:00 | 5.3 | Thu | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 3:00 | 5 | Thu | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 4:00 | 4.9 | Thu | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 5:00 | 3.7 | Thu | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 6:00 | 4.3 | Thu | School Day | Off | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 7:00 | 4.6 | Thu | School Day | On | On | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 4.8067
| 8:00 | 5.5 | Thu | School Day | On | On | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 4.5581
| 9:00 | 5.7 | Thu | School Day | On | On | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 4.5028
| 10:00 | 5.8 | Thu | School Day | On | On | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 4.4752
| 11:00 | 6.4 | Thu | School Day | On | On | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 4.3095
| 12:00 | 6.6 | Thu | School Day | On | On | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 4.2542
| 13:00 | 6.9 | Thu | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 14:00 | 7.4 | Thu | School Day | On | On | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 4.0332
| 15:00 | 7.5 | Thu | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 16:00 | 7.8 | Thu | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 17:00 | 7.9 | Thu | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 18:00 | 8 | Thu | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 19:00 | 8.3 | Thu | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 20:00 | 8.5 | Thu | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 21:00 | 7.8 | Thu | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 22:00 | 8.8 | Thu | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 23:00 | 9.1 | Thu | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
Fri, 18/Nov | 24:00 | 9.3 | Fri | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 1:00 | 8.6 | Fri | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 2:00 | 8.3 | Fri | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 3:00 | 9.2 | Fri | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 4:00 | 9.7 | Fri | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 5:00 | 10.1 | Fri | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 6:00 | 10.1 | Fri | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 7:00 | 9.9 | Fri | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 8:00 | 10 | Fri | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 9:00 | 9.5 | Fri | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 10:00 | 9.5 | Fri | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 11:00 | 11.6 | Fri | School Day | On | On | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 2.873
| 12:00 | 11.2 | Fri | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 13:00 | 12.6 | Fri | School Day | On | On | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 2.5967
| 14:00 | 12.7 | Fri | School Day | On | On | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 2.5691
| 15:00 | 13.4 | Fri | School Day | On | On | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 2.3757
| 16:00 | 12.9 | Fri | School Day | On | On | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 2.5138
| 17:00 | 11.8 | Fri | School Day | On | On | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 2.8177
| 18:00 | 10.2 | Fri | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 19:00 | 10.4 | Fri | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 20:00 | 10 | Fri | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 21:00 | 10.1 | Fri | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 22:00 | 9.7 | Fri | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 23:00 | 9.7 | Fri | School Day | Off | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
Sat, 19/Nov | 24:00 | 8.5 | Sat | WE | Off | OFF | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 1:00 | 9.2 | Sat | WE | Off | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 2:00 | 9.1 | Sat | WE | Off | OFF | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 3:00 | 8.9 | Sat | WE | Off | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 4:00 | 7.5 | Sat | WE | Off | OFF | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 5:00 | 7.8 | Sat | WE | Off | OFF | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 6:00 | 7.8 | Sat | WE | Off | OFF | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 7:00 | 7.5 | Sat | WE | On | OFF | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 8:00 | 7.2 | Sat | WE | On | OFF | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 9:00 | 7 | Sat | WE | On | OFF | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 10:00 | 8.1 | Sat | WE | On | OFF | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 11:00 | 9.7 | Sat | WE | On | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 12:00 | 11 | Sat | WE | On | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 13:00 | 12.6 | Sat | WE | On | OFF | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 14:00 | 13.6 | Sat | WE | On | OFF | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 15:00 | 13.3 | Sat | WE | On | OFF | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 16:00 | 13.1 | Sat | WE | On | OFF | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 17:00 | 12.6 | Sat | WE | On | OFF | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 18:00 | 12.2 | Sat | WE | On | OFF | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 19:00 | 12 | Sat | WE | Off | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 20:00 | 11.7 | Sat | WE | Off | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 21:00 | 11.5 | Sat | WE | Off | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 22:00 | 10.3 | Sat | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 23:00 | 10.7 | Sat | WE | Off | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
Sun, 20/Nov | 24:00 | 10.4 | Sun | WE | Off | OFF | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 1:00 | 9.8 | Sun | WE | Off | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 2:00 | 9.4 | Sun | WE | Off | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 3:00 | 9.3 | Sun | WE | Off | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 4:00 | 9 | Sun | WE | Off | OFF | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 5:00 | 8.9 | Sun | WE | Off | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 6:00 | 8.9 | Sun | WE | Off | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 7:00 | 9.2 | Sun | WE | On | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 8:00 | 9.7 | Sun | WE | On | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 9:00 | 9.9 | Sun | WE | On | OFF | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 10:00 | 10 | Sun | WE | On | OFF | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 11:00 | 10.7 | Sun | WE | On | OFF | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 12:00 | 11.5 | Sun | WE | On | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 13:00 | 12.4 | Sun | WE | On | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 14:00 | 12.8 | Sun | WE | On | OFF | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 15:00 | 12.8 | Sun | WE | On | OFF | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 16:00 | 12.5 | Sun | WE | On | OFF | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 17:00 | 11.4 | Sun | WE | On | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 18:00 | 10.1 | Sun | WE | On | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 19:00 | 10.5 | Sun | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 20:00 | 10.4 | Sun | WE | Off | OFF | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 21:00 | 9.3 | Sun | WE | Off | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 22:00 | 9.4 | Sun | WE | Off | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 23:00 | 9.2 | Sun | WE | Off | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
Mon, 21/Nov | 24:00 | 8.4 | Mon | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 1:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 2:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 3:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 4:00 | 8.1 | Mon | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 5:00 | 7.6 | Mon | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 6:00 | 7.4 | Mon | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 7:00 | 7.6 | Mon | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 8:00 | 7.8 | Mon | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 9:00 | 7.8 | Mon | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 10:00 | 8.3 | Mon | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 11:00 | 8.8 | Mon | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 12:00 | 9.3 | Mon | School Day | On | On | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 3.5083
| 13:00 | 9.8 | Mon | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 14:00 | 10.6 | Mon | School Day | On | On | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 3.1492
| 15:00 | 10.3 | Mon | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 16:00 | 10.5 | Mon | School Day | On | On | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 3.1768
| 17:00 | 10.4 | Mon | School Day | On | On | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 3.2045
| 18:00 | 10.3 | Mon | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 19:00 | 9.5 | Mon | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 20:00 | 9.3 | Mon | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 21:00 | 9.5 | Mon | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 22:00 | 10 | Mon | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 23:00 | 10.3 | Mon | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
Tue, 22/Nov | 24:00 | 10.6 | Tue | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 1:00 | 10.6 | Tue | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 2:00 | 10.6 | Tue | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 3:00 | 10.3 | Tue | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 4:00 | 10.2 | Tue | School Day | Off | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 5:00 | 9.6 | Tue | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 6:00 | 9.6 | Tue | School Day | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 7:00 | 9.5 | Tue | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 8:00 | 9.3 | Tue | School Day | On | On | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 3.5083
| 9:00 | 8.5 | Tue | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 10:00 | 8.4 | Tue | School Day | On | On | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 3.757
| 11:00 | 8.8 | Tue | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 12:00 | 10 | Tue | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 13:00 | 10.3 | Tue | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 14:00 | 10.3 | Tue | School Day | On | On | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 3.2321
| 15:00 | 10 | Tue | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 16:00 | 9.8 | Tue | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 17:00 | 9.4 | Tue | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 18:00 | 7.9 | Tue | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 19:00 | 7.1 | Tue | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 20:00 | 6.6 | Tue | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 21:00 | 6.1 | Tue | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 22:00 | 5.6 | Tue | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 23:00 | 5.4 | Tue | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
Wed, 23/Nov | 24:00 | 4.9 | Wed | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 1:00 | 4.4 | Wed | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 2:00 | 4.2 | Wed | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
| 3:00 | 3.9 | Wed | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 4:00 | 3.6 | Wed | School Day | Off | Off | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 5:00 | 3.7 | Wed | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 6:00 | 3.6 | Wed | School Day | Off | Off | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 7:00 | 3.5 | Wed | School Day | On | On | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 5.1106
| 8:00 | 3.7 | Wed | School Day | On | On | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 5.0553
| 9:00 | 3.7 | Wed | School Day | On | On | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 5.0553
| 10:00 | 4.6 | Wed | School Day | On | On | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 4.8067
| 11:00 | 6.1 | Wed | School Day | On | On | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 4.3923
| 12:00 | 7.1 | Wed | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 13:00 | 8 | Wed | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 14:00 | 8.6 | Wed | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 15:00 | 8.6 | Wed | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 16:00 | 8.2 | Wed | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 17:00 | 7.2 | Wed | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 18:00 | 6.2 | Wed | School Day | On | On | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 4.3647
| 19:00 | 5.3 | Wed | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 20:00 | 4.4 | Wed | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 21:00 | 3.2 | Wed | School Day | Off | Off | 22 | 20.12 | 1.88 | 1.7 | 3.591 | 0.25 | 1035 | 1.6024 | 0
| 22:00 | 3.1 | Wed | School Day | Off | Off | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 23:00 | 0.9 | Wed | School Day | Off | Off | 22 | 19.89 | 2.11 | 1.7 | 4.0303 | 0.25 | 1035 | 1.7985 | 0
Thu, 24/Nov | 24:00 | 1.7 | Thu | School Day | Off | Off | 22 | 19.97 | 2.03 | 1.7 | 3.8775 | 0.25 | 1035 | 1.7303 | 0
| 1:00 | 1 | Thu | School Day | Off | Off | 22 | 19.9 | 2.1 | 1.7 | 4.0112 | 0.25 | 1035 | 1.79 | 0
| 2:00 | -0.5 | Thu | School Day | Off | Off | 22 | 19.75 | 2.25 | 1.7 | 4.2977 | 0.25 | 1035 | 1.9178 | 0
| 3:00 | 0 | Thu | School Day | Off | Off | 22 | 19.8 | 2.2 | 1.7 | 4.2022 | 0.25 | 1035 | 1.8752 | 0
| 4:00 | -0.7 | Thu | School Day | Off | Off | 22 | 19.73 | 2.27 | 1.7 | 4.3359 | 0.25 | 1035 | 1.9349 | 0
| 5:00 | -1.3 | Thu | School Day | Off | Off | 22 | 19.67 | 2.33 | 1.7 | 4.4505 | 0.25 | 1035 | 1.986 | 0
| 6:00 | -1.5 | Thu | School Day | Off | Off | 22 | 19.65 | 2.35 | 1.7 | 4.4887 | 0.25 | 1035 | 2.0031 | 0
| 7:00 | -1 | Thu | School Day | On | On | 22 | 19.7 | 2.3 | 1.7 | 4.3932 | 0.25 | 1035 | 1.9604 | 6.3537
| 8:00 | -1.3 | Thu | School Day | On | On | 22 | 19.67 | 2.33 | 1.7 | 4.4505 | 0.25 | 1035 | 1.986 | 6.4366
| 9:00 | -1.7 | Thu | School Day | On | On | 22 | 19.63 | 2.37 | 1.7 | 4.5269 | 0.25 | 1035 | 2.0201 | 6.5471
| 10:00 | 0.5 | Thu | School Day | On | On | 22 | 19.85 | 2.15 | 1.7 | 4.1067 | 0.25 | 1035 | 1.8326 | 5.9393
| 11:00 | 2.1 | Thu | School Day | On | On | 22 | 20.01 | 1.99 | 1.7 | 3.8011 | 0.25 | 1035 | 1.6962 | 5.4973
| 12:00 | 3.3 | Thu | School Day | On | On | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 5.1658
| 13:00 | 6.3 | Thu | School Day | On | On | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 4.3371
| 14:00 | 7.9 | Thu | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 15:00 | 8 | Thu | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 16:00 | 7.8 | Thu | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 17:00 | 7.6 | Thu | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 18:00 | 7.2 | Thu | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 19:00 | 6.6 | Thu | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 20:00 | 6.4 | Thu | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 21:00 | 6.6 | Thu | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 22:00 | 6.2 | Thu | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 23:00 | 6.2 | Thu | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
Fri, 25/Nov | 24:00 | 6.2 | Fri | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 1:00 | 6.4 | Fri | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 2:00 | 6.1 | Fri | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 3:00 | 6.2 | Fri | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 4:00 | 6.5 | Fri | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 5:00 | 6.7 | Fri | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 6:00 | 5.6 | Fri | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 7:00 | 4.1 | Fri | School Day | On | On | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 4.9448
| 8:00 | 2.9 | Fri | School Day | On | On | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 5.2763
| 9:00 | 3.2 | Fri | School Day | On | On | 22 | 20.12 | 1.88 | 1.7 | 3.591 | 0.25 | 1035 | 1.6024 | 5.1934
| 10:00 | 4.1 | Fri | School Day | On | On | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 4.9448
| 11:00 | 5.4 | Fri | School Day | On | On | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 4.5857
| 12:00 | 6.3 | Fri | School Day | On | On | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 4.3371
| 13:00 | 6.6 | Fri | School Day | On | On | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 4.2542
| 14:00 | 6.9 | Fri | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 15:00 | 6.9 | Fri | School Day | On | On | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 4.1713
| 16:00 | 6.5 | Fri | School Day | On | On | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 4.2818
| 17:00 | 4.6 | Fri | School Day | On | On | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 4.8067
| 18:00 | 3.9 | Fri | School Day | On | On | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 5.0001
| 19:00 | 3.4 | Fri | School Day | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 20:00 | 2.1 | Fri | School Day | Off | Off | 22 | 20.01 | 1.99 | 1.7 | 3.8011 | 0.25 | 1035 | 1.6962 | 0
| 21:00 | 2.1 | Fri | School Day | Off | Off | 22 | 20.01 | 1.99 | 1.7 | 3.8011 | 0.25 | 1035 | 1.6962 | 0
| 22:00 | 1.4 | Fri | School Day | Off | Off | 22 | 19.94 | 2.06 | 1.7 | 3.9348 | 0.25 | 1035 | 1.7559 | 0
| 23:00 | 0.2 | Fri | School Day | Off | Off | 22 | 19.82 | 2.18 | 1.7 | 4.164 | 0.25 | 1035 | 1.8582 | 0
Sat, 26/Nov | 24:00 | -0.6 | Sat | WE | Off | OFF | 22 | 19.74 | 2.26 | 1.7 | 4.3168 | 0.25 | 1035 | 1.9263 | 0
| 1:00 | -1.3 | Sat | WE | Off | OFF | 22 | 19.67 | 2.33 | 1.7 | 4.4505 | 0.25 | 1035 | 1.986 | 0
| 2:00 | -1.8 | Sat | WE | Off | OFF | 22 | 19.62 | 2.38 | 1.7 | 4.546 | 0.25 | 1035 | 2.0286 | 0
| 3:00 | -2.9 | Sat | WE | Off | OFF | 22 | 19.51 | 2.49 | 1.7 | 4.7562 | 0.25 | 1035 | 2.1224 | 0
| 4:00 | -3 | Sat | WE | Off | OFF | 22 | 19.5 | 2.5 | 1.7 | 4.7753 | 0.25 | 1035 | 2.1309 | 0
| 5:00 | -3.7 | Sat | WE | Off | OFF | 22 | 19.43 | 2.57 | 1.7 | 4.909 | 0.25 | 1035 | 2.1906 | 0
| 6:00 | -3.6 | Sat | WE | Off | OFF | 22 | 19.44 | 2.56 | 1.7 | 4.8899 | 0.25 | 1035 | 2.1821 | 0
| 7:00 | -3.7 | Sat | WE | On | OFF | 22 | 19.43 | 2.57 | 1.7 | 4.909 | 0.25 | 1035 | 2.1906 | 0
| 8:00 | -2.9 | Sat | WE | On | OFF | 22 | 19.51 | 2.49 | 1.7 | 4.7562 | 0.25 | 1035 | 2.1224 | 0
| 9:00 | -3.7 | Sat | WE | On | OFF | 22 | 19.43 | 2.57 | 1.7 | 4.909 | 0.25 | 1035 | 2.1906 | 0
| 10:00 | -2 | Sat | WE | On | OFF | 22 | 19.6 | 2.4 | 1.7 | 4.5842 | 0.25 | 1035 | 2.0457 | 0
| 11:00 | 0.4 | Sat | WE | On | OFF | 22 | 19.84 | 2.16 | 1.7 | 4.1258 | 0.25 | 1035 | 1.8411 | 0
| 12:00 | 2.5 | Sat | WE | On | OFF | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 13:00 | 4.7 | Sat | WE | On | OFF | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 14:00 | 6.1 | Sat | WE | On | OFF | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 15:00 | 7.4 | Sat | WE | On | OFF | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 16:00 | 7.4 | Sat | WE | On | OFF | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 17:00 | 6.5 | Sat | WE | On | OFF | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 18:00 | 2.6 | Sat | WE | On | OFF | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 0
| 19:00 | 3.8 | Sat | WE | Off | OFF | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 20:00 | 3 | Sat | WE | Off | OFF | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 21:00 | 2.4 | Sat | WE | Off | OFF | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 22:00 | 1.9 | Sat | WE | Off | OFF | 22 | 19.99 | 2.01 | 1.7 | 3.8393 | 0.25 | 1035 | 1.7133 | 0
| 23:00 | 1.8 | Sat | WE | Off | OFF | 22 | 19.98 | 2.02 | 1.7 | 3.8584 | 0.25 | 1035 | 1.7218 | 0
Sun, 27/Nov | 24:00 | 2.1 | Sun | WE | Off | OFF | 22 | 20.01 | 1.99 | 1.7 | 3.8011 | 0.25 | 1035 | 1.6962 | 0
| 1:00 | 2.3 | Sun | WE | Off | OFF | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 0
| 2:00 | 1.6 | Sun | WE | Off | OFF | 22 | 19.96 | 2.04 | 1.7 | 3.8966 | 0.25 | 1035 | 1.7388 | 0
| 3:00 | 0.5 | Sun | WE | Off | OFF | 22 | 19.85 | 2.15 | 1.7 | 4.1067 | 0.25 | 1035 | 1.8326 | 0
| 4:00 | 0.3 | Sun | WE | Off | OFF | 22 | 19.83 | 2.17 | 1.7 | 4.1449 | 0.25 | 1035 | 1.8496 | 0
| 5:00 | -0.5 | Sun | WE | Off | OFF | 22 | 19.75 | 2.25 | 1.7 | 4.2977 | 0.25 | 1035 | 1.9178 | 0
| 6:00 | -0.7 | Sun | WE | Off | OFF | 22 | 19.73 | 2.27 | 1.7 | 4.3359 | 0.25 | 1035 | 1.9349 | 0
| 7:00 | -1.1 | Sun | WE | On | OFF | 22 | 19.69 | 2.31 | 1.7 | 4.4123 | 0.25 | 1035 | 1.969 | 0
| 8:00 | -0.2 | Sun | WE | On | OFF | 22 | 19.78 | 2.22 | 1.7 | 4.2404 | 0.25 | 1035 | 1.8923 | 0
| 9:00 | 0.6 | Sun | WE | On | OFF | 22 | 19.86 | 2.14 | 1.7 | 4.0876 | 0.25 | 1035 | 1.8241 | 0
| 10:00 | 0.9 | Sun | WE | On | OFF | 22 | 19.89 | 2.11 | 1.7 | 4.0303 | 0.25 | 1035 | 1.7985 | 0
| 11:00 | 1.9 | Sun | WE | On | OFF | 22 | 19.99 | 2.01 | 1.7 | 3.8393 | 0.25 | 1035 | 1.7133 | 0
| 12:00 | 4.3 | Sun | WE | On | OFF | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 13:00 | 6 | Sun | WE | On | OFF | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 14:00 | 6.9 | Sun | WE | On | OFF | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 15:00 | 7.9 | Sun | WE | On | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 16:00 | 8.1 | Sun | WE | On | OFF | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 17:00 | 7.2 | Sun | WE | On | OFF | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 18:00 | 6.2 | Sun | WE | On | OFF | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 19:00 | 5.5 | Sun | WE | Off | OFF | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 20:00 | 4.5 | Sun | WE | Off | OFF | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 21:00 | 3.7 | Sun | WE | Off | OFF | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 22:00 | 2.5 | Sun | WE | Off | OFF | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 23:00 | 2.2 | Sun | WE | Off | OFF | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 0
Mon, 28/Nov | 24:00 | 1.2 | Mon | School Day | Off | Off | 22 | 19.92 | 2.08 | 1.7 | 3.973 | 0.25 | 1035 | 1.7729 | 0
| 1:00 | 0.6 | Mon | School Day | Off | Off | 22 | 19.86 | 2.14 | 1.7 | 4.0876 | 0.25 | 1035 | 1.8241 | 0
| 2:00 | -0.1 | Mon | School Day | Off | Off | 22 | 19.79 | 2.21 | 1.7 | 4.2213 | 0.25 | 1035 | 1.8837 | 0
| 3:00 | -0.9 | Mon | School Day | Off | Off | 22 | 19.71 | 2.29 | 1.7 | 4.3741 | 0.25 | 1035 | 1.9519 | 0
| 4:00 | -1.4 | Mon | School Day | Off | Off | 22 | 19.66 | 2.34 | 1.7 | 4.4696 | 0.25 | 1035 | 1.9945 | 0
| 5:00 | -1.4 | Mon | School Day | Off | Off | 22 | 19.66 | 2.34 | 1.7 | 4.4696 | 0.25 | 1035 | 1.9945 | 0
| 6:00 | -1.8 | Mon | School Day | Off | Off | 22 | 19.62 | 2.38 | 1.7 | 4.546 | 0.25 | 1035 | 2.0286 | 0
| 7:00 | -0.8 | Mon | School Day | On | On | 22 | 19.72 | 2.28 | 1.7 | 4.355 | 0.25 | 1035 | 1.9434 | 6.2984
| 8:00 | -0.2 | Mon | School Day | On | On | 22 | 19.78 | 2.22 | 1.7 | 4.2404 | 0.25 | 1035 | 1.8923 | 6.1327
| 9:00 | 0.6 | Mon | School Day | On | On | 22 | 19.86 | 2.14 | 1.7 | 4.0876 | 0.25 | 1035 | 1.8241 | 5.9117
| 10:00 | 1.7 | Mon | School Day | On | On | 22 | 19.97 | 2.03 | 1.7 | 3.8775 | 0.25 | 1035 | 1.7303 | 5.6078
| 11:00 | 2 | Mon | School Day | On | On | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 5.5249
| 12:00 | 2.7 | Mon | School Day | On | On | 22 | 20.07 | 1.93 | 1.7 | 3.6865 | 0.25 | 1035 | 1.6451 | 5.3316
| 13:00 | 3.6 | Mon | School Day | On | On | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 5.0829
| 14:00 | 5 | Mon | School Day | On | On | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 4.6962
| 15:00 | 5.8 | Mon | School Day | On | On | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 4.4752
| 16:00 | 6.2 | Mon | School Day | On | On | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 4.3647
| 17:00 | 6.4 | Mon | School Day | On | On | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 4.3095
| 18:00 | 6.5 | Mon | School Day | On | On | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 4.2818
| 19:00 | 6.6 | Mon | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 20:00 | 7.1 | Mon | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 21:00 | 7 | Mon | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 22:00 | 7.3 | Mon | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 23:00 | 7.5 | Mon | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
Tue, 29/Nov | 24:00 | 7.4 | Tue | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 1:00 | 6.7 | Tue | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 2:00 | 6 | Tue | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 3:00 | 5.2 | Tue | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 4:00 | 4 | Tue | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 5:00 | 3.7 | Tue | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 6:00 | 2.9 | Tue | School Day | Off | Off | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 7:00 | 2.4 | Tue | School Day | On | On | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 5.4144
| 8:00 | 2.4 | Tue | School Day | On | On | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 5.4144
| 9:00 | 2.2 | Tue | School Day | On | On | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 5.4697
| 10:00 | 2.8 | Tue | School Day | On | On | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 5.3039
| 11:00 | 4.9 | Tue | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 12:00 | 6.7 | Tue | School Day | On | On | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 4.2266
| 13:00 | 8.5 | Tue | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 14:00 | 9 | Tue | School Day | On | On | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 3.5912
| 15:00 | 9 | Tue | School Day | On | On | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 3.5912
| 16:00 | 8.6 | Tue | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 17:00 | 7.3 | Tue | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 18:00 | 6.5 | Tue | School Day | On | On | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 4.2818
| 19:00 | 6 | Tue | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 20:00 | 5.1 | Tue | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 21:00 | 4.4 | Tue | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 22:00 | 4 | Tue | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 23:00 | 3.4 | Tue | School Day | Off | Off | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
Wed, 30/Nov | 24:00 | 2.7 | Wed | School Day | Off | Off | 22 | 20.07 | 1.93 | 1.7 | 3.6865 | 0.25 | 1035 | 1.6451 | 0
| 1:00 | 1.8 | Wed | School Day | Off | Off | 22 | 19.98 | 2.02 | 1.7 | 3.8584 | 0.25 | 1035 | 1.7218 | 0
| 2:00 | 1.9 | Wed | School Day | Off | Off | 22 | 19.99 | 2.01 | 1.7 | 3.8393 | 0.25 | 1035 | 1.7133 | 0
| 3:00 | 1.4 | Wed | School Day | Off | Off | 22 | 19.94 | 2.06 | 1.7 | 3.9348 | 0.25 | 1035 | 1.7559 | 0
| 4:00 | 0.7 | Wed | School Day | Off | Off | 22 | 19.87 | 2.13 | 1.7 | 4.0685 | 0.25 | 1035 | 1.8155 | 0
| 5:00 | 0.7 | Wed | School Day | Off | Off | 22 | 19.87 | 2.13 | 1.7 | 4.0685 | 0.25 | 1035 | 1.8155 | 0
| 6:00 | 0.6 | Wed | School Day | Off | Off | 22 | 19.86 | 2.14 | 1.7 | 4.0876 | 0.25 | 1035 | 1.8241 | 0
| 7:00 | 0.7 | Wed | School Day | On | On | 22 | 19.87 | 2.13 | 1.7 | 4.0685 | 0.25 | 1035 | 1.8155 | 5.8841
| 8:00 | 0.9 | Wed | School Day | On | On | 22 | 19.89 | 2.11 | 1.7 | 4.0303 | 0.25 | 1035 | 1.7985 | 5.8288
| 9:00 | 1.2 | Wed | School Day | On | On | 22 | 19.92 | 2.08 | 1.7 | 3.973 | 0.25 | 1035 | 1.7729 | 5.7459
| 10:00 | 2.1 | Wed | School Day | On | On | 22 | 20.01 | 1.99 | 1.7 | 3.8011 | 0.25 | 1035 | 1.6962 | 5.4973
| 11:00 | 3.7 | Wed | School Day | On | On | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 5.0553
| 12:00 | 5.8 | Wed | School Day | On | On | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 4.4752
| 13:00 | 7.7 | Wed | School Day | On | On | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 3.9503
| 14:00 | 8.9 | Wed | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 15:00 | 8.5 | Wed | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 16:00 | 8.1 | Wed | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 17:00 | 7.2 | Wed | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 18:00 | 5.9 | Wed | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 19:00 | 5.2 | Wed | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 20:00 | 4.4 | Wed | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 21:00 | 3.9 | Wed | School Day | Off | Off | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 22:00 | 3.3 | Wed | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 23:00 | 2.7 | Wed | School Day | Off | Off | 22 | 20.07 | 1.93 | 1.7 | 3.6865 | 0.25 | 1035 | 1.6451 | 0
Thu, 01/Dec | 24:00 | 2.5 | Thu | School Day | Off | Off | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 1:00 | 2.2 | Thu | School Day | Off | Off | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 0
| 2:00 | 1.4 | Thu | School Day | Off | Off | 22 | 19.94 | 2.06 | 1.7 | 3.9348 | 0.25 | 1035 | 1.7559 | 0
| 3:00 | 1 | Thu | School Day | Off | Off | 22 | 19.9 | 2.1 | 1.7 | 4.0112 | 0.25 | 1035 | 1.79 | 0
| 4:00 | 0.6 | Thu | School Day | Off | Off | 22 | 19.86 | 2.14 | 1.7 | 4.0876 | 0.25 | 1035 | 1.8241 | 0
| 5:00 | 0.5 | Thu | School Day | Off | Off | 22 | 19.85 | 2.15 | 1.7 | 4.1067 | 0.25 | 1035 | 1.8326 | 0
| 6:00 | 0.2 | Thu | School Day | Off | Off | 22 | 19.82 | 2.18 | 1.7 | 4.164 | 0.25 | 1035 | 1.8582 | 0
| 7:00 | -0.5 | Thu | School Day | On | On | 22 | 19.75 | 2.25 | 1.7 | 4.2977 | 0.25 | 1035 | 1.9178 | 6.2156
| 8:00 | 0.2 | Thu | School Day | On | On | 22 | 19.82 | 2.18 | 1.7 | 4.164 | 0.25 | 1035 | 1.8582 | 6.0222
| 9:00 | 0.1 | Thu | School Day | On | On | 22 | 19.81 | 2.19 | 1.7 | 4.1831 | 0.25 | 1035 | 1.8667 | 6.0498
| 10:00 | 0.3 | Thu | School Day | On | On | 22 | 19.83 | 2.17 | 1.7 | 4.1449 | 0.25 | 1035 | 1.8496 | 5.9946
| 11:00 | 1.4 | Thu | School Day | On | On | 22 | 19.94 | 2.06 | 1.7 | 3.9348 | 0.25 | 1035 | 1.7559 | 5.6907
| 12:00 | 2.6 | Thu | School Day | On | On | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 5.3592
| 13:00 | 3.5 | Thu | School Day | On | On | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 5.1106
| 14:00 | 4.3 | Thu | School Day | On | On | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 4.8896
| 15:00 | 4.9 | Thu | School Day | On | On | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 4.7238
| 16:00 | 5 | Thu | School Day | On | On | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 4.6962
| 17:00 | 4.3 | Thu | School Day | On | On | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 4.8896
| 18:00 | 3.6 | Thu | School Day | On | On | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 5.0829
| 19:00 | 3.7 | Thu | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 20:00 | 4.1 | Thu | School Day | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 21:00 | 3.7 | Thu | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 22:00 | 3.8 | Thu | School Day | Off | Off | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 23:00 | 4.2 | Thu | School Day | Off | Off | 22 | 20.22 | 1.78 | 1.7 | 3.4 | 0.25 | 1035 | 1.5172 | 0
Fri, 02/Dec | 24:00 | 4.4 | Fri | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 1:00 | 4.4 | Fri | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 2:00 | 4.5 | Fri | School Day | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 3:00 | 4.6 | Fri | School Day | Off | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 4:00 | 4.5 | Fri | School Day | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 5:00 | 4.9 | Fri | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 6:00 | 4.6 | Fri | School Day | Off | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 7:00 | 4.5 | Fri | School Day | On | On | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 4.8343
| 8:00 | 4 | Fri | School Day | On | On | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 4.9724
| 9:00 | 3.4 | Fri | School Day | On | On | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 5.1382
| 10:00 | 3.6 | Fri | School Day | On | On | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 5.0829
| 11:00 | 4.6 | Fri | School Day | On | On | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 4.8067
| 12:00 | 5 | Fri | School Day | On | On | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 4.6962
| 13:00 | 5.6 | Fri | School Day | On | On | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 4.5304
| 14:00 | 6.6 | Fri | School Day | On | On | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 4.2542
| 15:00 | 7.1 | Fri | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 16:00 | 7.1 | Fri | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 17:00 | 6.8 | Fri | School Day | On | On | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 4.199
| 18:00 | 7 | Fri | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 19:00 | 6.9 | Fri | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 20:00 | 6.2 | Fri | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 21:00 | 6.5 | Fri | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 22:00 | 6.3 | Fri | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 23:00 | 5.8 | Fri | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
Sat, 03/Dec | 24:00 | 5.7 | Sat | WE | Off | OFF | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 1:00 | 5.5 | Sat | WE | Off | OFF | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 2:00 | 4.7 | Sat | WE | Off | OFF | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 3:00 | 4.5 | Sat | WE | Off | OFF | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 4:00 | 4.1 | Sat | WE | Off | OFF | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 5:00 | 3.4 | Sat | WE | Off | OFF | 22 | 20.14 | 1.86 | 1.7 | 3.5528 | 0.25 | 1035 | 1.5854 | 0
| 6:00 | 2.6 | Sat | WE | Off | OFF | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 0
| 7:00 | 2.4 | Sat | WE | On | OFF | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 8:00 | 2.4 | Sat | WE | On | OFF | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 9:00 | 2.4 | Sat | WE | On | OFF | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 10:00 | 3 | Sat | WE | On | OFF | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 11:00 | 3.6 | Sat | WE | On | OFF | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 12:00 | 4 | Sat | WE | On | OFF | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 13:00 | 5.1 | Sat | WE | On | OFF | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 14:00 | 5.7 | Sat | WE | On | OFF | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 15:00 | 6.3 | Sat | WE | On | OFF | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 16:00 | 5.9 | Sat | WE | On | OFF | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 17:00 | 5.2 | Sat | WE | On | OFF | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 18:00 | 4.5 | Sat | WE | On | OFF | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 19:00 | 4 | Sat | WE | Off | OFF | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 20:00 | 3.2 | Sat | WE | Off | OFF | 22 | 20.12 | 1.88 | 1.7 | 3.591 | 0.25 | 1035 | 1.6024 | 0
| 21:00 | 2.7 | Sat | WE | Off | OFF | 22 | 20.07 | 1.93 | 1.7 | 3.6865 | 0.25 | 1035 | 1.6451 | 0
| 22:00 | 2.5 | Sat | WE | Off | OFF | 22 | 20.05 | 1.95 | 1.7 | 3.7247 | 0.25 | 1035 | 1.6621 | 0
| 23:00 | 2 | Sat | WE | Off | OFF | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 0
Sun, 04/Dec | 24:00 | 2 | Sun | WE | Off | OFF | 22 | 20 | 2 | 1.7 | 3.8202 | 0.25 | 1035 | 1.7047 | 0
| 1:00 | 2.8 | Sun | WE | Off | OFF | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 2:00 | 3.5 | Sun | WE | Off | OFF | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 3:00 | 3.3 | Sun | WE | Off | OFF | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 4:00 | 2.6 | Sun | WE | Off | OFF | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 0
| 5:00 | 2.2 | Sun | WE | Off | OFF | 22 | 20.02 | 1.98 | 1.7 | 3.782 | 0.25 | 1035 | 1.6877 | 0
| 6:00 | 2.1 | Sun | WE | Off | OFF | 22 | 20.01 | 1.99 | 1.7 | 3.8011 | 0.25 | 1035 | 1.6962 | 0
| 7:00 | 3.5 | Sun | WE | On | OFF | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 8:00 | 4.1 | Sun | WE | On | OFF | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 9:00 | 5.1 | Sun | WE | On | OFF | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 10:00 | 6 | Sun | WE | On | OFF | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 11:00 | 6.5 | Sun | WE | On | OFF | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 12:00 | 6.8 | Sun | WE | On | OFF | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 13:00 | 6.7 | Sun | WE | On | OFF | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 14:00 | 6.8 | Sun | WE | On | OFF | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 15:00 | 7.5 | Sun | WE | On | OFF | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 16:00 | 7.9 | Sun | WE | On | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 17:00 | 7.1 | Sun | WE | On | OFF | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 18:00 | 6 | Sun | WE | On | OFF | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 19:00 | 5.4 | Sun | WE | Off | OFF | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 20:00 | 5.7 | Sun | WE | Off | OFF | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 21:00 | 7.5 | Sun | WE | Off | OFF | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 22:00 | 7.6 | Sun | WE | Off | OFF | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 23:00 | 8.4 | Sun | WE | Off | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
Mon, 05/Dec | 24:00 | 8.1 | Mon | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 1:00 | 8.6 | Mon | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 2:00 | 8.6 | Mon | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 3:00 | 8.1 | Mon | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 4:00 | 6.7 | Mon | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 5:00 | 6.1 | Mon | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 6:00 | 7 | Mon | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 7:00 | 7.9 | Mon | School Day | On | On | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 3.8951
| 8:00 | 8.6 | Mon | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 9:00 | 8.5 | Mon | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 10:00 | 8.6 | Mon | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 11:00 | 8.8 | Mon | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 12:00 | 9.3 | Mon | School Day | On | On | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 3.5083
| 13:00 | 10.2 | Mon | School Day | On | On | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 3.2597
| 14:00 | 9.8 | Mon | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 15:00 | 9.9 | Mon | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 16:00 | 10 | Mon | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 17:00 | 9.5 | Mon | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 18:00 | 9.5 | Mon | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 19:00 | 8.6 | Mon | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 20:00 | 7.7 | Mon | School Day | Off | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 21:00 | 7 | Mon | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 22:00 | 6.9 | Mon | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 23:00 | 6.5 | Mon | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
Tue, 06/Dec | 24:00 | 5.6 | Tue | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 1:00 | 5.1 | Tue | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 2:00 | 5.4 | Tue | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 3:00 | 6.5 | Tue | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 4:00 | 7 | Tue | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 5:00 | 7.3 | Tue | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 6:00 | 5.9 | Tue | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 7:00 | 6.4 | Tue | School Day | On | On | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 4.3095
| 8:00 | 6.2 | Tue | School Day | On | On | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 4.3647
| 9:00 | 8.1 | Tue | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 10:00 | 8.4 | Tue | School Day | On | On | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 3.757
| 11:00 | 8.6 | Tue | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 12:00 | 9.1 | Tue | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 13:00 | 9.2 | Tue | School Day | On | On | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 3.536
| 14:00 | 9.5 | Tue | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 15:00 | 9.9 | Tue | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 16:00 | 9.8 | Tue | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 17:00 | 9.4 | Tue | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 18:00 | 9.1 | Tue | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 19:00 | 8.5 | Tue | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 20:00 | 7.2 | Tue | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 21:00 | 7.1 | Tue | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 22:00 | 7.1 | Tue | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 23:00 | 7 | Tue | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
Wed, 07/Dec | 24:00 | 6.8 | Wed | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 1:00 | 6.4 | Wed | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 2:00 | 6 | Wed | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 3:00 | 6 | Wed | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 4:00 | 5.9 | Wed | School Day | Off | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 5:00 | 6 | Wed | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 6:00 | 7.1 | Wed | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 7:00 | 7.7 | Wed | School Day | On | On | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 3.9503
| 8:00 | 7.8 | Wed | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 9:00 | 8.1 | Wed | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 10:00 | 8.1 | Wed | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 11:00 | 8.1 | Wed | School Day | On | On | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 3.8398
| 12:00 | 8.5 | Wed | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 13:00 | 8.5 | Wed | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 14:00 | 8.6 | Wed | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 15:00 | 8.9 | Wed | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 16:00 | 8.8 | Wed | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 17:00 | 8.5 | Wed | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 18:00 | 8.3 | Wed | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 19:00 | 8.2 | Wed | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 20:00 | 8.1 | Wed | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 21:00 | 8.1 | Wed | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 22:00 | 7.8 | Wed | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 23:00 | 7.8 | Wed | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
Thu, 08/Dec | 24:00 | 7.5 | Thu | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 1:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 2:00 | 7.5 | Thu | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 3:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 4:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 5:00 | 7.5 | Thu | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 6:00 | 7.4 | Thu | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 7:00 | 7.4 | Thu | School Day | On | On | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 4.0332
| 8:00 | 7.3 | Thu | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 9:00 | 7.2 | Thu | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 10:00 | 6.7 | Thu | School Day | On | On | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 4.2266
| 11:00 | 7.3 | Thu | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 12:00 | 7.6 | Thu | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 13:00 | 7.6 | Thu | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 14:00 | 7.6 | Thu | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 15:00 | 8 | Thu | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 16:00 | 8 | Thu | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 17:00 | 7.8 | Thu | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 18:00 | 7.5 | Thu | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 19:00 | 7.5 | Thu | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 20:00 | 7.1 | Thu | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 21:00 | 6 | Thu | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 22:00 | 5.2 | Thu | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 23:00 | 4 | Thu | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
Fri, 09/Dec | 24:00 | 4 | Fri | School Day | Off | Off | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 1:00 | 3.3 | Fri | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 2:00 | 2.8 | Fri | School Day | Off | Off | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 3:00 | 2.8 | Fri | School Day | Off | Off | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 4:00 | 2.8 | Fri | School Day | Off | Off | 22 | 20.08 | 1.92 | 1.7 | 3.6674 | 0.25 | 1035 | 1.6365 | 0
| 5:00 | 2.1 | Fri | School Day | Off | Off | 22 | 20.01 | 1.99 | 1.7 | 3.8011 | 0.25 | 1035 | 1.6962 | 0
| 6:00 | 2.3 | Fri | School Day | Off | Off | 22 | 20.03 | 1.97 | 1.7 | 3.7629 | 0.25 | 1035 | 1.6792 | 0
| 7:00 | 3.3 | Fri | School Day | On | On | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 5.1658
| 8:00 | 4.1 | Fri | School Day | On | On | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 4.9448
| 9:00 | 4.6 | Fri | School Day | On | On | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 4.8067
| 10:00 | 5.2 | Fri | School Day | On | On | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 4.6409
| 11:00 | 5.8 | Fri | School Day | On | On | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 4.4752
| 12:00 | 6.7 | Fri | School Day | On | On | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 4.2266
| 13:00 | 6.4 | Fri | School Day | On | On | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 4.3095
| 14:00 | 7.3 | Fri | School Day | On | On | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 4.0608
| 15:00 | 8 | Fri | School Day | On | On | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 3.8675
| 16:00 | 7.8 | Fri | School Day | On | On | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 3.9227
| 17:00 | 7.1 | Fri | School Day | On | On | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 4.1161
| 18:00 | 6.1 | Fri | School Day | On | On | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 4.3923
| 19:00 | 5.7 | Fri | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 20:00 | 5.8 | Fri | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 21:00 | 6.2 | Fri | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 22:00 | 6.3 | Fri | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 23:00 | 6.1 | Fri | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
Sat, 10/Dec | 24:00 | 5.9 | Sat | WE | Off | OFF | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 1:00 | 4.7 | Sat | WE | Off | OFF | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 2:00 | 3.6 | Sat | WE | Off | OFF | 22 | 20.16 | 1.84 | 1.7 | 3.5146 | 0.25 | 1035 | 1.5684 | 0
| 3:00 | 2.4 | Sat | WE | Off | OFF | 22 | 20.04 | 1.96 | 1.7 | 3.7438 | 0.25 | 1035 | 1.6706 | 0
| 4:00 | 2.6 | Sat | WE | Off | OFF | 22 | 20.06 | 1.94 | 1.7 | 3.7056 | 0.25 | 1035 | 1.6536 | 0
| 5:00 | 3 | Sat | WE | Off | OFF | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 6:00 | 2.9 | Sat | WE | Off | OFF | 22 | 20.09 | 1.91 | 1.7 | 3.6483 | 0.25 | 1035 | 1.628 | 0
| 7:00 | 3 | Sat | WE | On | OFF | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 8:00 | 3.2 | Sat | WE | On | OFF | 22 | 20.12 | 1.88 | 1.7 | 3.591 | 0.25 | 1035 | 1.6024 | 0
| 9:00 | 3.5 | Sat | WE | On | OFF | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 10:00 | 3.7 | Sat | WE | On | OFF | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 11:00 | 4.3 | Sat | WE | On | OFF | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 12:00 | 4.9 | Sat | WE | On | OFF | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 13:00 | 5.6 | Sat | WE | On | OFF | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 14:00 | 6.6 | Sat | WE | On | OFF | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 15:00 | 7.4 | Sat | WE | On | OFF | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 16:00 | 7 | Sat | WE | On | OFF | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 17:00 | 6.9 | Sat | WE | On | OFF | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 18:00 | 5.9 | Sat | WE | On | OFF | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 19:00 | 6.4 | Sat | WE | Off | OFF | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 20:00 | 6.3 | Sat | WE | Off | OFF | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 21:00 | 6.4 | Sat | WE | Off | OFF | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 22:00 | 6.3 | Sat | WE | Off | OFF | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 23:00 | 5.8 | Sat | WE | Off | OFF | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
Sun, 11/Dec | 24:00 | 5.8 | Sun | WE | Off | OFF | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 1:00 | 5.2 | Sun | WE | Off | OFF | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 2:00 | 4.8 | Sun | WE | Off | OFF | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 3:00 | 5.3 | Sun | WE | Off | OFF | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 4:00 | 4.9 | Sun | WE | Off | OFF | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 5:00 | 4.6 | Sun | WE | Off | OFF | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 6:00 | 4.1 | Sun | WE | Off | OFF | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 7:00 | 3.9 | Sun | WE | On | OFF | 22 | 20.19 | 1.81 | 1.7 | 3.4573 | 0.25 | 1035 | 1.5428 | 0
| 8:00 | 4.4 | Sun | WE | On | OFF | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 9:00 | 4.3 | Sun | WE | On | OFF | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 10:00 | 4.1 | Sun | WE | On | OFF | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 11:00 | 5.1 | Sun | WE | On | OFF | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 12:00 | 5.8 | Sun | WE | On | OFF | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 13:00 | 8.1 | Sun | WE | On | OFF | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 14:00 | 8.4 | Sun | WE | On | OFF | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 15:00 | 8 | Sun | WE | On | OFF | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 16:00 | 6.9 | Sun | WE | On | OFF | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 17:00 | 5.3 | Sun | WE | On | OFF | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 18:00 | 5 | Sun | WE | On | OFF | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 19:00 | 3.8 | Sun | WE | Off | OFF | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 20:00 | 4.5 | Sun | WE | Off | OFF | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 21:00 | 4 | Sun | WE | Off | OFF | 22 | 20.2 | 1.8 | 1.7 | 3.4382 | 0.25 | 1035 | 1.5343 | 0
| 22:00 | 3.8 | Sun | WE | Off | OFF | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
| 23:00 | 3.8 | Sun | WE | Off | OFF | 22 | 20.18 | 1.82 | 1.7 | 3.4764 | 0.25 | 1035 | 1.5513 | 0
Mon, 12/Dec | 24:00 | 3.5 | Mon | School Day | Off | Off | 22 | 20.15 | 1.85 | 1.7 | 3.5337 | 0.25 | 1035 | 1.5769 | 0
| 1:00 | 3 | Mon | School Day | Off | Off | 22 | 20.1 | 1.9 | 1.7 | 3.6292 | 0.25 | 1035 | 1.6195 | 0
| 2:00 | 3.1 | Mon | School Day | Off | Off | 22 | 20.11 | 1.89 | 1.7 | 3.6101 | 0.25 | 1035 | 1.611 | 0
| 3:00 | 3.3 | Mon | School Day | Off | Off | 22 | 20.13 | 1.87 | 1.7 | 3.5719 | 0.25 | 1035 | 1.5939 | 0
| 4:00 | 3.7 | Mon | School Day | Off | Off | 22 | 20.17 | 1.83 | 1.7 | 3.4955 | 0.25 | 1035 | 1.5598 | 0
| 5:00 | 4.4 | Mon | School Day | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 6:00 | 4.8 | Mon | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 7:00 | 5.9 | Mon | School Day | On | On | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 4.4476
| 8:00 | 7 | Mon | School Day | On | On | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 4.1437
| 9:00 | 8.5 | Mon | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 10:00 | 9.4 | Mon | School Day | On | On | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 3.4807
| 11:00 | 9.5 | Mon | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 12:00 | 9.5 | Mon | School Day | On | On | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 3.4531
| 13:00 | 9.8 | Mon | School Day | On | On | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 3.3702
| 14:00 | 10 | Mon | School Day | On | On | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 3.315
| 15:00 | 9.9 | Mon | School Day | On | On | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 3.3426
| 16:00 | 9.1 | Mon | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 17:00 | 8.6 | Mon | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 18:00 | 8.5 | Mon | School Day | On | On | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 3.7293
| 19:00 | 8.4 | Mon | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 20:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 21:00 | 8.8 | Mon | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 22:00 | 8.7 | Mon | School Day | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 23:00 | 7.9 | Mon | School Day | Off | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
Tue, 13/Dec | 24:00 | 7.2 | Tue | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 1:00 | 4.9 | Tue | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 2:00 | 5.3 | Tue | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 3:00 | 5.1 | Tue | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 4:00 | 5 | Tue | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 5:00 | 4.6 | Tue | School Day | Off | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 6:00 | 5 | Tue | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 7:00 | 6 | Tue | School Day | On | On | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 4.4199
| 8:00 | 6.5 | Tue | School Day | On | On | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 4.2818
| 9:00 | 6.6 | Tue | School Day | On | On | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 4.2542
| 10:00 | 6.7 | Tue | School Day | On | On | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 4.2266
| 11:00 | 7.2 | Tue | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 12:00 | 6.8 | Tue | School Day | On | On | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 4.199
| 13:00 | 7.4 | Tue | School Day | On | On | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 4.0332
| 14:00 | 8.6 | Tue | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 15:00 | 10.8 | Tue | School Day | On | On | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 3.094
| 16:00 | 12 | Tue | School Day | On | On | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 2.7625
| 17:00 | 12.3 | Tue | School Day | On | On | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 2.6796
| 18:00 | 12.1 | Tue | School Day | On | On | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 2.7348
| 19:00 | 12.3 | Tue | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 20:00 | 12 | Tue | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 21:00 | 11.9 | Tue | School Day | Off | Off | 22 | 20.99 | 1.01 | 1.7 | 1.9292 | 0.25 | 1035 | 0.86089 | 0
| 22:00 | 12.3 | Tue | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 23:00 | 12.6 | Tue | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
Wed, 14/Dec | 24:00 | 12 | Wed | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 1:00 | 10.3 | Wed | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 2:00 | 9.4 | Wed | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 3:00 | 8.8 | Wed | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 4:00 | 8.6 | Wed | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 5:00 | 8.6 | Wed | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 6:00 | 9.5 | Wed | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 7:00 | 10.9 | Wed | School Day | On | On | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 3.0663
| 8:00 | 11 | Wed | School Day | On | On | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 3.0387
| 9:00 | 11.7 | Wed | School Day | On | On | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 2.8453
| 10:00 | 12.4 | Wed | School Day | On | On | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 2.652
| 11:00 | 13.6 | Wed | School Day | On | On | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 2.3205
| 12:00 | 14.3 | Wed | School Day | On | On | 22 | 21.23 | 0.77 | 1.7 | 1.4708 | 0.25 | 1035 | 0.65632 | 2.1271
| 13:00 | 14.4 | Wed | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 14:00 | 13.8 | Wed | School Day | On | On | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 2.2652
| 15:00 | 13.7 | Wed | School Day | On | On | 22 | 21.17 | 0.83 | 1.7 | 1.5854 | 0.25 | 1035 | 0.70746 | 2.2928
| 16:00 | 13.1 | Wed | School Day | On | On | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 2.4586
| 17:00 | 13.2 | Wed | School Day | On | On | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 2.431
| 18:00 | 12.6 | Wed | School Day | On | On | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 2.5967
| 19:00 | 13 | Wed | School Day | Off | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 20:00 | 13.1 | Wed | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 21:00 | 12.7 | Wed | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 22:00 | 12.3 | Wed | School Day | Off | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 23:00 | 12.6 | Wed | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
Thu, 15/Dec | 24:00 | 12.5 | Thu | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 1:00 | 9.5 | Thu | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 2:00 | 9.1 | Thu | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 3:00 | 9 | Thu | School Day | Off | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 4:00 | 8.5 | Thu | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 5:00 | 8.1 | Thu | School Day | Off | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 6:00 | 7.6 | Thu | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 7:00 | 7.6 | Thu | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 8:00 | 7.5 | Thu | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 9:00 | 7.6 | Thu | School Day | On | On | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 3.978
| 10:00 | 7.5 | Thu | School Day | On | On | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 4.0056
| 11:00 | 8.2 | Thu | School Day | On | On | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 3.8122
| 12:00 | 8.6 | Thu | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 13:00 | 8.9 | Thu | School Day | On | On | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 3.6188
| 14:00 | 9.1 | Thu | School Day | On | On | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 3.5636
| 15:00 | 8.8 | Thu | School Day | On | On | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 3.6465
| 16:00 | 8.3 | Thu | School Day | On | On | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 3.7846
| 17:00 | 8.6 | Thu | School Day | On | On | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 3.7017
| 18:00 | 7.2 | Thu | School Day | On | On | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 4.0885
| 19:00 | 8.2 | Thu | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 20:00 | 8.5 | Thu | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 21:00 | 8.5 | Thu | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 22:00 | 8.6 | Thu | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 23:00 | 8.9 | Thu | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
Fri, 16/Dec | 24:00 | 8.8 | Fri | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 1:00 | 9.1 | Fri | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 2:00 | 9.1 | Fri | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 3:00 | 9.1 | Fri | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 4:00 | 9.4 | Fri | School Day | Off | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 5:00 | 9.5 | Fri | School Day | Off | Off | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 6:00 | 9.8 | Fri | School Day | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 7:00 | 10.1 | Fri | School Day | On | On | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 3.2873
| 8:00 | 11.2 | Fri | School Day | On | On | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 2.9835
| 9:00 | 13.9 | Fri | School Day | On | On | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 2.2376
| 10:00 | 13.9 | Fri | School Day | On | On | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 2.2376
| 11:00 | 14.2 | Fri | School Day | On | On | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 2.1547
| 12:00 | 14.1 | Fri | School Day | On | On | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 2.1824
| 13:00 | 14.2 | Fri | School Day | On | On | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 2.1547
| 14:00 | 14.4 | Fri | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 15:00 | 14.4 | Fri | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 16:00 | 14.4 | Fri | School Day | On | On | 22 | 21.24 | 0.76 | 1.7 | 1.4517 | 0.25 | 1035 | 0.6478 | 2.0995
| 17:00 | 13.6 | Fri | School Day | On | On | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 2.3205
| 18:00 | 13.2 | Fri | School Day | On | On | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 2.431
| 19:00 | 13.5 | Fri | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 20:00 | 13.5 | Fri | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 21:00 | 13.5 | Fri | School Day | Off | Off | 22 | 21.15 | 0.85 | 1.7 | 1.6236 | 0.25 | 1035 | 0.72451 | 0
| 22:00 | 13.4 | Fri | School Day | Off | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 23:00 | 13.1 | Fri | School Day | Off | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
Sat, 17/Dec | 24:00 | 13.1 | Sat | WE | Off | OFF | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 1:00 | 13.2 | Sat | WE | Off | OFF | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 2:00 | 13 | Sat | WE | Off | OFF | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 3:00 | 12.4 | Sat | WE | Off | OFF | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 4:00 | 12.9 | Sat | WE | Off | OFF | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 5:00 | 12 | Sat | WE | Off | OFF | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 6:00 | 11.8 | Sat | WE | Off | OFF | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 7:00 | 11.1 | Sat | WE | On | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 8:00 | 11.7 | Sat | WE | On | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 9:00 | 12.3 | Sat | WE | On | OFF | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 10:00 | 12.7 | Sat | WE | On | OFF | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 11:00 | 12.2 | Sat | WE | On | OFF | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 12:00 | 12.8 | Sat | WE | On | OFF | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 13:00 | 13.1 | Sat | WE | On | OFF | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 14:00 | 12.9 | Sat | WE | On | OFF | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 15:00 | 12.5 | Sat | WE | On | OFF | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
| 16:00 | 11.4 | Sat | WE | On | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 17:00 | 11.5 | Sat | WE | On | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 18:00 | 10.4 | Sat | WE | On | OFF | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 19:00 | 10.5 | Sat | WE | Off | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 20:00 | 10.3 | Sat | WE | Off | OFF | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 21:00 | 9.6 | Sat | WE | Off | OFF | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 22:00 | 9.7 | Sat | WE | Off | OFF | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 23:00 | 9.8 | Sat | WE | Off | OFF | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
Sun, 18/Dec | 24:00 | 9.3 | Sun | WE | Off | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 1:00 | 8.9 | Sun | WE | Off | OFF | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 2:00 | 8.7 | Sun | WE | Off | OFF | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 3:00 | 7.9 | Sun | WE | Off | OFF | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 4:00 | 7.4 | Sun | WE | Off | OFF | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 5:00 | 8.6 | Sun | WE | Off | OFF | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 6:00 | 9.4 | Sun | WE | Off | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 7:00 | 9.3 | Sun | WE | On | OFF | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 8:00 | 9.2 | Sun | WE | On | OFF | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 9:00 | 9.4 | Sun | WE | On | OFF | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 10:00 | 9.5 | Sun | WE | On | OFF | 22 | 20.75 | 1.25 | 1.7 | 2.3876 | 0.25 | 1035 | 1.0655 | 0
| 11:00 | 10.1 | Sun | WE | On | OFF | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 12:00 | 10.5 | Sun | WE | On | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 13:00 | 11.2 | Sun | WE | On | OFF | 22 | 20.92 | 1.08 | 1.7 | 2.0629 | 0.25 | 1035 | 0.92055 | 0
| 14:00 | 11.1 | Sun | WE | On | OFF | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 15:00 | 10.9 | Sun | WE | On | OFF | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 16:00 | 10.6 | Sun | WE | On | OFF | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 17:00 | 10.5 | Sun | WE | On | OFF | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 18:00 | 11 | Sun | WE | On | OFF | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 19:00 | 11.4 | Sun | WE | Off | OFF | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 20:00 | 11.5 | Sun | WE | Off | OFF | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 21:00 | 12.2 | Sun | WE | Off | OFF | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 22:00 | 11.7 | Sun | WE | Off | OFF | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 23:00 | 11.6 | Sun | WE | Off | OFF | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
Mon, 19/Dec | 24:00 | 11 | Mon | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 1:00 | 7.3 | Mon | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 2:00 | 4.6 | Mon | School Day | Off | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 3:00 | 4.8 | Mon | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 4:00 | 5.3 | Mon | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 5:00 | 5.1 | Mon | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 6:00 | 4.9 | Mon | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 7:00 | 5.1 | Mon | School Day | On | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 8:00 | 4.3 | Mon | School Day | On | Off | 22 | 20.23 | 1.77 | 1.7 | 3.3809 | 0.25 | 1035 | 1.5087 | 0
| 9:00 | 5.4 | Mon | School Day | On | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 10:00 | 5.5 | Mon | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 11:00 | 5.5 | Mon | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 12:00 | 6.1 | Mon | School Day | On | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 13:00 | 7 | Mon | School Day | On | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 14:00 | 8.5 | Mon | School Day | On | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 15:00 | 7.4 | Mon | School Day | On | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 16:00 | 7.3 | Mon | School Day | On | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 17:00 | 6.7 | Mon | School Day | On | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 18:00 | 6 | Mon | School Day | On | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 19:00 | 5.7 | Mon | School Day | Off | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 20:00 | 6.1 | Mon | School Day | Off | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 21:00 | 6.8 | Mon | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 22:00 | 7.5 | Mon | School Day | Off | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 23:00 | 7.2 | Mon | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
Tue, 20/Dec | 24:00 | 6.6 | Tue | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 1:00 | 6.2 | Tue | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 2:00 | 6.6 | Tue | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 3:00 | 7.6 | Tue | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 4:00 | 8.8 | Tue | School Day | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 5:00 | 10.6 | Tue | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 6:00 | 12.2 | Tue | School Day | Off | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 7:00 | 12.7 | Tue | School Day | On | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 8:00 | 13 | Tue | School Day | On | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 9:00 | 13.2 | Tue | School Day | On | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 10:00 | 13.1 | Tue | School Day | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 11:00 | 13.3 | Tue | School Day | On | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 12:00 | 14 | Tue | School Day | On | Off | 22 | 21.2 | 0.8 | 1.7 | 1.5281 | 0.25 | 1035 | 0.68189 | 0
| 13:00 | 14.9 | Tue | School Day | On | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 14:00 | 15.5 | Tue | School Day | On | Off | 22 | 21.35 | 0.65 | 1.7 | 1.2416 | 0.25 | 1035 | 0.55404 | 0
| 15:00 | 14.8 | Tue | School Day | On | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 16:00 | 14.9 | Tue | School Day | On | Off | 22 | 21.29 | 0.71 | 1.7 | 1.3562 | 0.25 | 1035 | 0.60518 | 0
| 17:00 | 14.5 | Tue | School Day | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 18:00 | 13.6 | Tue | School Day | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 19:00 | 13.2 | Tue | School Day | Off | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 20:00 | 14.6 | Tue | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 21:00 | 13.9 | Tue | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 22:00 | 11.8 | Tue | School Day | Off | Off | 22 | 20.98 | 1.02 | 1.7 | 1.9483 | 0.25 | 1035 | 0.86941 | 0
| 23:00 | 12.5 | Tue | School Day | Off | Off | 22 | 21.05 | 0.95 | 1.7 | 1.8146 | 0.25 | 1035 | 0.80975 | 0
Wed, 21/Dec | 24:00 | 13.8 | Wed | School Day | Off | Off | 22 | 21.18 | 0.82 | 1.7 | 1.5663 | 0.25 | 1035 | 0.69894 | 0
| 1:00 | 13.9 | Wed | School Day | Off | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 2:00 | 14.2 | Wed | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 3:00 | 14.6 | Wed | School Day | Off | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 4:00 | 14.1 | Wed | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 5:00 | 14.2 | Wed | School Day | Off | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 6:00 | 14.1 | Wed | School Day | Off | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 7:00 | 14.5 | Wed | School Day | On | Off | 22 | 21.25 | 0.75 | 1.7 | 1.4326 | 0.25 | 1035 | 0.63927 | 0
| 8:00 | 14.1 | Wed | School Day | On | Off | 22 | 21.21 | 0.79 | 1.7 | 1.509 | 0.25 | 1035 | 0.67337 | 0
| 9:00 | 14.6 | Wed | School Day | On | Off | 22 | 21.26 | 0.74 | 1.7 | 1.4135 | 0.25 | 1035 | 0.63075 | 0
| 10:00 | 14.2 | Wed | School Day | On | Off | 22 | 21.22 | 0.78 | 1.7 | 1.4899 | 0.25 | 1035 | 0.66485 | 0
| 11:00 | 13.9 | Wed | School Day | On | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 12:00 | 14.7 | Wed | School Day | On | Off | 22 | 21.27 | 0.73 | 1.7 | 1.3944 | 0.25 | 1035 | 0.62223 | 0
| 13:00 | 15 | Wed | School Day | On | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 14:00 | 15 | Wed | School Day | On | Off | 22 | 21.3 | 0.7 | 1.7 | 1.3371 | 0.25 | 1035 | 0.59666 | 0
| 15:00 | 14.8 | Wed | School Day | On | Off | 22 | 21.28 | 0.72 | 1.7 | 1.3753 | 0.25 | 1035 | 0.6137 | 0
| 16:00 | 13.9 | Wed | School Day | On | Off | 22 | 21.19 | 0.81 | 1.7 | 1.5472 | 0.25 | 1035 | 0.69042 | 0
| 17:00 | 13.3 | Wed | School Day | On | Off | 22 | 21.13 | 0.87 | 1.7 | 1.6618 | 0.25 | 1035 | 0.74156 | 0
| 18:00 | 13 | Wed | School Day | On | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 19:00 | 12.9 | Wed | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 20:00 | 12.9 | Wed | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 21:00 | 12.6 | Wed | School Day | Off | Off | 22 | 21.06 | 0.94 | 1.7 | 1.7955 | 0.25 | 1035 | 0.80122 | 0
| 22:00 | 12.7 | Wed | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 23:00 | 12.9 | Wed | School Day | Off | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
Thu, 22/Dec | 24:00 | 12.7 | Thu | School Day | Off | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 1:00 | 12 | Thu | School Day | Off | Off | 22 | 21 | 1 | 1.7 | 1.9101 | 0.25 | 1035 | 0.85237 | 0
| 2:00 | 11.5 | Thu | School Day | Off | Off | 22 | 20.95 | 1.05 | 1.7 | 2.0056 | 0.25 | 1035 | 0.89498 | 0
| 3:00 | 11.1 | Thu | School Day | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 4:00 | 10.9 | Thu | School Day | Off | Off | 22 | 20.89 | 1.11 | 1.7 | 2.1202 | 0.25 | 1035 | 0.94613 | 0
| 5:00 | 10.6 | Thu | School Day | Off | Off | 22 | 20.86 | 1.14 | 1.7 | 2.1775 | 0.25 | 1035 | 0.9717 | 0
| 6:00 | 10.5 | Thu | School Day | Off | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 7:00 | 10.1 | Thu | School Day | On | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 8:00 | 9.6 | Thu | School Day | On | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 9:00 | 9 | Thu | School Day | On | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 10:00 | 8.2 | Thu | School Day | On | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 11:00 | 9.4 | Thu | School Day | On | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 12:00 | 9.6 | Thu | School Day | On | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 13:00 | 9.2 | Thu | School Day | On | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 14:00 | 9.8 | Thu | School Day | On | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 15:00 | 9.9 | Thu | School Day | On | Off | 22 | 20.79 | 1.21 | 1.7 | 2.3112 | 0.25 | 1035 | 1.0314 | 0
| 16:00 | 9.4 | Thu | School Day | On | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 17:00 | 8.6 | Thu | School Day | On | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 18:00 | 6.6 | Thu | School Day | On | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 19:00 | 6 | Thu | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 20:00 | 6 | Thu | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 21:00 | 5.8 | Thu | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 22:00 | 5.1 | Thu | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 23:00 | 5.5 | Thu | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
Fri, 23/Dec | 24:00 | 4.8 | Fri | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 1:00 | 4.5 | Fri | School Day | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 2:00 | 5.1 | Fri | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 3:00 | 5.3 | Fri | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 4:00 | 5.4 | Fri | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 5:00 | 5.8 | Fri | School Day | Off | Off | 22 | 20.38 | 1.62 | 1.7 | 3.0944 | 0.25 | 1035 | 1.3808 | 0
| 6:00 | 6.3 | Fri | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 7:00 | 6.6 | Fri | School Day | On | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 8:00 | 7.5 | Fri | School Day | On | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 9:00 | 8.1 | Fri | School Day | On | Off | 22 | 20.61 | 1.39 | 1.7 | 2.655 | 0.25 | 1035 | 1.1848 | 0
| 10:00 | 8.8 | Fri | School Day | On | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 11:00 | 9.2 | Fri | School Day | On | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 12:00 | 9.6 | Fri | School Day | On | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 13:00 | 8.7 | Fri | School Day | On | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 14:00 | 9.6 | Fri | School Day | On | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 15:00 | 10.2 | Fri | School Day | On | Off | 22 | 20.82 | 1.18 | 1.7 | 2.2539 | 0.25 | 1035 | 1.0058 | 0
| 16:00 | 9.7 | Fri | School Day | On | Off | 22 | 20.77 | 1.23 | 1.7 | 2.3494 | 0.25 | 1035 | 1.0484 | 0
| 17:00 | 10.1 | Fri | School Day | On | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 18:00 | 10 | Fri | School Day | On | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 19:00 | 10 | Fri | School Day | Off | Off | 22 | 20.8 | 1.2 | 1.7 | 2.2921 | 0.25 | 1035 | 1.0228 | 0
| 20:00 | 10.1 | Fri | School Day | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 21:00 | 10.3 | Fri | School Day | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 22:00 | 10.4 | Fri | School Day | Off | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 23:00 | 11 | Fri | School Day | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
Sat, 24/Dec | 24:00 | 11.6 | Sat | WE | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 1:00 | 11.1 | Sat | WE | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 2:00 | 10.8 | Sat | WE | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 3:00 | 10.3 | Sat | WE | Off | Off | 22 | 20.83 | 1.17 | 1.7 | 2.2348 | 0.25 | 1035 | 0.99727 | 0
| 4:00 | 10.1 | Sat | WE | Off | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 5:00 | 11.1 | Sat | WE | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 6:00 | 11.7 | Sat | WE | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 7:00 | 12.4 | Sat | WE | On | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 8:00 | 12.8 | Sat | WE | On | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 9:00 | 12.9 | Sat | WE | On | Off | 22 | 21.09 | 0.91 | 1.7 | 1.7382 | 0.25 | 1035 | 0.77565 | 0
| 10:00 | 12.8 | Sat | WE | On | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 11:00 | 13.1 | Sat | WE | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 12:00 | 13.2 | Sat | WE | On | Off | 22 | 21.12 | 0.88 | 1.7 | 1.6809 | 0.25 | 1035 | 0.75008 | 0
| 13:00 | 13.1 | Sat | WE | On | Off | 22 | 21.11 | 0.89 | 1.7 | 1.7 | 0.25 | 1035 | 0.75861 | 0
| 14:00 | 13.4 | Sat | WE | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 15:00 | 13.4 | Sat | WE | On | Off | 22 | 21.14 | 0.86 | 1.7 | 1.6427 | 0.25 | 1035 | 0.73303 | 0
| 16:00 | 13.6 | Sat | WE | On | Off | 22 | 21.16 | 0.84 | 1.7 | 1.6045 | 0.25 | 1035 | 0.71599 | 0
| 17:00 | 12.7 | Sat | WE | On | Off | 22 | 21.07 | 0.93 | 1.7 | 1.7764 | 0.25 | 1035 | 0.7927 | 0
| 18:00 | 13 | Sat | WE | On | Off | 22 | 21.1 | 0.9 | 1.7 | 1.7191 | 0.25 | 1035 | 0.76713 | 0
| 19:00 | 12.8 | Sat | WE | Off | Off | 22 | 21.08 | 0.92 | 1.7 | 1.7573 | 0.25 | 1035 | 0.78418 | 0
| 20:00 | 12.4 | Sat | WE | Off | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 21:00 | 11.7 | Sat | WE | Off | Off | 22 | 20.97 | 1.03 | 1.7 | 1.9674 | 0.25 | 1035 | 0.87794 | 0
| 22:00 | 10.8 | Sat | WE | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 23:00 | 11 | Sat | WE | Off | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
Sun, 25/Dec | 24:00 | 10.8 | Sun | WE | Off | Off | 22 | 20.88 | 1.12 | 1.7 | 2.1393 | 0.25 | 1035 | 0.95465 | 0
| 1:00 | 11.1 | Sun | WE | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 2:00 | 11.1 | Sun | WE | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 3:00 | 11.1 | Sun | WE | Off | Off | 22 | 20.91 | 1.09 | 1.7 | 2.082 | 0.25 | 1035 | 0.92908 | 0
| 4:00 | 11.4 | Sun | WE | Off | Off | 22 | 20.94 | 1.06 | 1.7 | 2.0247 | 0.25 | 1035 | 0.90351 | 0
| 5:00 | 11.6 | Sun | WE | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 6:00 | 11.6 | Sun | WE | Off | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 7:00 | 11.3 | Sun | WE | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 8:00 | 11.3 | Sun | WE | On | Off | 22 | 20.93 | 1.07 | 1.7 | 2.0438 | 0.25 | 1035 | 0.91203 | 0
| 9:00 | 10.5 | Sun | WE | On | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 10:00 | 10.5 | Sun | WE | On | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 11:00 | 11 | Sun | WE | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 12:00 | 11.6 | Sun | WE | On | Off | 22 | 20.96 | 1.04 | 1.7 | 1.9865 | 0.25 | 1035 | 0.88646 | 0
| 13:00 | 12.4 | Sun | WE | On | Off | 22 | 21.04 | 0.96 | 1.7 | 1.8337 | 0.25 | 1035 | 0.81827 | 0
| 14:00 | 12.3 | Sun | WE | On | Off | 22 | 21.03 | 0.97 | 1.7 | 1.8528 | 0.25 | 1035 | 0.82679 | 0
| 15:00 | 12.2 | Sun | WE | On | Off | 22 | 21.02 | 0.98 | 1.7 | 1.8719 | 0.25 | 1035 | 0.83532 | 0
| 16:00 | 12.1 | Sun | WE | On | Off | 22 | 21.01 | 0.99 | 1.7 | 1.891 | 0.25 | 1035 | 0.84384 | 0
| 17:00 | 10.5 | Sun | WE | On | Off | 22 | 20.85 | 1.15 | 1.7 | 2.1966 | 0.25 | 1035 | 0.98022 | 0
| 18:00 | 10.1 | Sun | WE | On | Off | 22 | 20.81 | 1.19 | 1.7 | 2.273 | 0.25 | 1035 | 1.0143 | 0
| 19:00 | 9.6 | Sun | WE | Off | Off | 22 | 20.76 | 1.24 | 1.7 | 2.3685 | 0.25 | 1035 | 1.0569 | 0
| 20:00 | 9.8 | Sun | WE | Off | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 21:00 | 8.7 | Sun | WE | Off | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 22:00 | 9.1 | Sun | WE | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 23:00 | 8.8 | Sun | WE | Off | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
Mon, 26/Dec | 24:00 | 8.5 | Mon | School Day | Off | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 1:00 | 8 | Mon | School Day | Off | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 2:00 | 8.2 | Mon | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 3:00 | 7.8 | Mon | School Day | Off | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 4:00 | 6.9 | Mon | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 5:00 | 5.5 | Mon | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 6:00 | 6.7 | Mon | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 7:00 | 6.4 | Mon | School Day | On | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 8:00 | 6.3 | Mon | School Day | On | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 9:00 | 6.8 | Mon | School Day | On | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
| 10:00 | 6.5 | Mon | School Day | On | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 11:00 | 6.7 | Mon | School Day | On | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 12:00 | 7.7 | Mon | School Day | On | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 13:00 | 8.5 | Mon | School Day | On | Off | 22 | 20.65 | 1.35 | 1.7 | 2.5786 | 0.25 | 1035 | 1.1507 | 0
| 14:00 | 10.4 | Mon | School Day | On | Off | 22 | 20.84 | 1.16 | 1.7 | 2.2157 | 0.25 | 1035 | 0.98874 | 0
| 15:00 | 11 | Mon | School Day | On | Off | 22 | 20.9 | 1.1 | 1.7 | 2.1011 | 0.25 | 1035 | 0.9376 | 0
| 16:00 | 10.7 | Mon | School Day | On | Off | 22 | 20.87 | 1.13 | 1.7 | 2.1584 | 0.25 | 1035 | 0.96317 | 0
| 17:00 | 9.8 | Mon | School Day | On | Off | 22 | 20.78 | 1.22 | 1.7 | 2.3303 | 0.25 | 1035 | 1.0399 | 0
| 18:00 | 8.7 | Mon | School Day | On | Off | 22 | 20.67 | 1.33 | 1.7 | 2.5404 | 0.25 | 1035 | 1.1336 | 0
| 19:00 | 7.6 | Mon | School Day | Off | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 20:00 | 7.2 | Mon | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 21:00 | 7 | Mon | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 22:00 | 6.9 | Mon | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 23:00 | 6.8 | Mon | School Day | Off | Off | 22 | 20.48 | 1.52 | 1.7 | 2.9034 | 0.25 | 1035 | 1.2956 | 0
Tue, 27/Dec | 24:00 | 7 | Tue | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 1:00 | 7.2 | Tue | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 2:00 | 7.3 | Tue | School Day | Off | Off | 22 | 20.53 | 1.47 | 1.7 | 2.8079 | 0.25 | 1035 | 1.253 | 0
| 3:00 | 7.2 | Tue | School Day | Off | Off | 22 | 20.52 | 1.48 | 1.7 | 2.827 | 0.25 | 1035 | 1.2615 | 0
| 4:00 | 6.3 | Tue | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 5:00 | 6.4 | Tue | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 6:00 | 6.3 | Tue | School Day | Off | Off | 22 | 20.43 | 1.57 | 1.7 | 2.9989 | 0.25 | 1035 | 1.3382 | 0
| 7:00 | 5.3 | Tue | School Day | On | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 8:00 | 5.7 | Tue | School Day | On | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 9:00 | 6.6 | Tue | School Day | On | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 10:00 | 7.1 | Tue | School Day | On | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 11:00 | 7.5 | Tue | School Day | On | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 12:00 | 7.4 | Tue | School Day | On | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 13:00 | 8 | Tue | School Day | On | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 14:00 | 8.8 | Tue | School Day | On | Off | 22 | 20.68 | 1.32 | 1.7 | 2.5213 | 0.25 | 1035 | 1.1251 | 0
| 15:00 | 9 | Tue | School Day | On | Off | 22 | 20.7 | 1.3 | 1.7 | 2.4831 | 0.25 | 1035 | 1.1081 | 0
| 16:00 | 9.4 | Tue | School Day | On | Off | 22 | 20.74 | 1.26 | 1.7 | 2.4067 | 0.25 | 1035 | 1.074 | 0
| 17:00 | 9.1 | Tue | School Day | On | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
| 18:00 | 9.3 | Tue | School Day | On | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 19:00 | 9.3 | Tue | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 20:00 | 9.3 | Tue | School Day | Off | Off | 22 | 20.73 | 1.27 | 1.7 | 2.4258 | 0.25 | 1035 | 1.0825 | 0
| 21:00 | 9.2 | Tue | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 22:00 | 9.2 | Tue | School Day | Off | Off | 22 | 20.72 | 1.28 | 1.7 | 2.4449 | 0.25 | 1035 | 1.091 | 0
| 23:00 | 9.1 | Tue | School Day | Off | Off | 22 | 20.71 | 1.29 | 1.7 | 2.464 | 0.25 | 1035 | 1.0996 | 0
Wed, 28/Dec | 24:00 | 8.9 | Wed | School Day | Off | Off | 22 | 20.69 | 1.31 | 1.7 | 2.5022 | 0.25 | 1035 | 1.1166 | 0
| 1:00 | 8.6 | Wed | School Day | Off | Off | 22 | 20.66 | 1.34 | 1.7 | 2.5595 | 0.25 | 1035 | 1.1422 | 0
| 2:00 | 8.4 | Wed | School Day | Off | Off | 22 | 20.64 | 1.36 | 1.7 | 2.5977 | 0.25 | 1035 | 1.1592 | 0
| 3:00 | 8.3 | Wed | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 4:00 | 8.2 | Wed | School Day | Off | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 5:00 | 8.3 | Wed | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 6:00 | 8.3 | Wed | School Day | Off | Off | 22 | 20.63 | 1.37 | 1.7 | 2.6168 | 0.25 | 1035 | 1.1677 | 0
| 7:00 | 8.2 | Wed | School Day | On | Off | 22 | 20.62 | 1.38 | 1.7 | 2.6359 | 0.25 | 1035 | 1.1763 | 0
| 8:00 | 7.8 | Wed | School Day | On | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 9:00 | 7.6 | Wed | School Day | On | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 10:00 | 7.9 | Wed | School Day | On | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 11:00 | 7.7 | Wed | School Day | On | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 12:00 | 8 | Wed | School Day | On | Off | 22 | 20.6 | 1.4 | 1.7 | 2.6741 | 0.25 | 1035 | 1.1933 | 0
| 13:00 | 7.7 | Wed | School Day | On | Off | 22 | 20.57 | 1.43 | 1.7 | 2.7314 | 0.25 | 1035 | 1.2189 | 0
| 14:00 | 7.9 | Wed | School Day | On | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 15:00 | 7.9 | Wed | School Day | On | Off | 22 | 20.59 | 1.41 | 1.7 | 2.6932 | 0.25 | 1035 | 1.2018 | 0
| 16:00 | 7.8 | Wed | School Day | On | Off | 22 | 20.58 | 1.42 | 1.7 | 2.7123 | 0.25 | 1035 | 1.2104 | 0
| 17:00 | 7.6 | Wed | School Day | On | Off | 22 | 20.56 | 1.44 | 1.7 | 2.7505 | 0.25 | 1035 | 1.2274 | 0
| 18:00 | 7.5 | Wed | School Day | On | Off | 22 | 20.55 | 1.45 | 1.7 | 2.7696 | 0.25 | 1035 | 1.2359 | 0
| 19:00 | 7.4 | Wed | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 20:00 | 7.4 | Wed | School Day | Off | Off | 22 | 20.54 | 1.46 | 1.7 | 2.7888 | 0.25 | 1035 | 1.2445 | 0
| 21:00 | 7.1 | Wed | School Day | Off | Off | 22 | 20.51 | 1.49 | 1.7 | 2.8461 | 0.25 | 1035 | 1.27 | 0
| 22:00 | 7 | Wed | School Day | Off | Off | 22 | 20.5 | 1.5 | 1.7 | 2.8652 | 0.25 | 1035 | 1.2785 | 0
| 23:00 | 6.9 | Wed | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
Thu, 29/Dec | 24:00 | 6.9 | Thu | School Day | Off | Off | 22 | 20.49 | 1.51 | 1.7 | 2.8843 | 0.25 | 1035 | 1.2871 | 0
| 1:00 | 6.7 | Thu | School Day | Off | Off | 22 | 20.47 | 1.53 | 1.7 | 2.9225 | 0.25 | 1035 | 1.3041 | 0
| 2:00 | 6.6 | Thu | School Day | Off | Off | 22 | 20.46 | 1.54 | 1.7 | 2.9416 | 0.25 | 1035 | 1.3126 | 0
| 3:00 | 6.5 | Thu | School Day | Off | Off | 22 | 20.45 | 1.55 | 1.7 | 2.9607 | 0.25 | 1035 | 1.3212 | 0
| 4:00 | 6.4 | Thu | School Day | Off | Off | 22 | 20.44 | 1.56 | 1.7 | 2.9798 | 0.25 | 1035 | 1.3297 | 0
| 5:00 | 6.2 | Thu | School Day | Off | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 6:00 | 6 | Thu | School Day | Off | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 7:00 | 6 | Thu | School Day | On | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 8:00 | 6 | Thu | School Day | On | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 9:00 | 6 | Thu | School Day | On | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 10:00 | 6 | Thu | School Day | On | Off | 22 | 20.4 | 1.6 | 1.7 | 3.0562 | 0.25 | 1035 | 1.3638 | 0
| 11:00 | 6.1 | Thu | School Day | On | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 12:00 | 6.2 | Thu | School Day | On | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 13:00 | 6.2 | Thu | School Day | On | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 14:00 | 6.2 | Thu | School Day | On | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 15:00 | 6.2 | Thu | School Day | On | Off | 22 | 20.42 | 1.58 | 1.7 | 3.018 | 0.25 | 1035 | 1.3467 | 0
| 16:00 | 6.1 | Thu | School Day | On | Off | 22 | 20.41 | 1.59 | 1.7 | 3.0371 | 0.25 | 1035 | 1.3553 | 0
| 17:00 | 5.9 | Thu | School Day | On | Off | 22 | 20.39 | 1.61 | 1.7 | 3.0753 | 0.25 | 1035 | 1.3723 | 0
| 18:00 | 5.7 | Thu | School Day | On | Off | 22 | 20.37 | 1.63 | 1.7 | 3.1135 | 0.25 | 1035 | 1.3894 | 0
| 19:00 | 5.6 | Thu | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 20:00 | 5.6 | Thu | School Day | Off | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 21:00 | 5.1 | Thu | School Day | Off | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 22:00 | 5 | Thu | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 23:00 | 5 | Thu | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
Fri, 30/Dec | 24:00 | 4.9 | Fri | School Day | Off | Off | 22 | 20.29 | 1.71 | 1.7 | 3.2663 | 0.25 | 1035 | 1.4575 | 0
| 1:00 | 5.2 | Fri | School Day | Off | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 2:00 | 5.3 | Fri | School Day | Off | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 3:00 | 5.5 | Fri | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 4:00 | 5.4 | Fri | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 5:00 | 5.5 | Fri | School Day | Off | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 6:00 | 5.4 | Fri | School Day | Off | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 7:00 | 5.5 | Fri | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 8:00 | 5.6 | Fri | School Day | On | Off | 22 | 20.36 | 1.64 | 1.7 | 3.1326 | 0.25 | 1035 | 1.3979 | 0
| 9:00 | 5.5 | Fri | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 10:00 | 5.5 | Fri | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 11:00 | 5.5 | Fri | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 12:00 | 5.5 | Fri | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 13:00 | 5.5 | Fri | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 14:00 | 5.5 | Fri | School Day | On | Off | 22 | 20.35 | 1.65 | 1.7 | 3.1517 | 0.25 | 1035 | 1.4064 | 0
| 15:00 | 5.4 | Fri | School Day | On | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 16:00 | 5.2 | Fri | School Day | On | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 17:00 | 5.1 | Fri | School Day | On | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 18:00 | 4.8 | Fri | School Day | On | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 19:00 | 4.8 | Fri | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 20:00 | 5 | Fri | School Day | Off | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 21:00 | 4.8 | Fri | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 22:00 | 4.8 | Fri | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 23:00 | 4.8 | Fri | School Day | Off | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
Sat, 31/Dec | 24:00 | 4.7 | Sat | WE | Off | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 1:00 | 4.7 | Sat | WE | Off | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 2:00 | 4.6 | Sat | WE | Off | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 3:00 | 4.5 | Sat | WE | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 4:00 | 4.5 | Sat | WE | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 5:00 | 4.5 | Sat | WE | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 6:00 | 4.5 | Sat | WE | Off | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 7:00 | 4.6 | Sat | WE | On | Off | 22 | 20.26 | 1.74 | 1.7 | 3.3236 | 0.25 | 1035 | 1.4831 | 0
| 8:00 | 4.5 | Sat | WE | On | Off | 22 | 20.25 | 1.75 | 1.7 | 3.3427 | 0.25 | 1035 | 1.4916 | 0
| 9:00 | 4.4 | Sat | WE | On | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 10:00 | 5 | Sat | WE | On | Off | 22 | 20.3 | 1.7 | 1.7 | 3.2472 | 0.25 | 1035 | 1.449 | 0
| 11:00 | 5.1 | Sat | WE | On | Off | 22 | 20.31 | 1.69 | 1.7 | 3.2281 | 0.25 | 1035 | 1.4405 | 0
| 12:00 | 5.2 | Sat | WE | On | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 13:00 | 5.4 | Sat | WE | On | Off | 22 | 20.34 | 1.66 | 1.7 | 3.1708 | 0.25 | 1035 | 1.4149 | 0
| 14:00 | 5.3 | Sat | WE | On | Off | 22 | 20.33 | 1.67 | 1.7 | 3.1899 | 0.25 | 1035 | 1.4235 | 0
| 15:00 | 5.2 | Sat | WE | On | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 16:00 | 5.2 | Sat | WE | On | Off | 22 | 20.32 | 1.68 | 1.7 | 3.209 | 0.25 | 1035 | 1.432 | 0
| 17:00 | 4.8 | Sat | WE | On | Off | 22 | 20.28 | 1.72 | 1.7 | 3.2854 | 0.25 | 1035 | 1.4661 | 0
| 18:00 | 4.7 | Sat | WE | On | Off | 22 | 20.27 | 1.73 | 1.7 | 3.3045 | 0.25 | 1035 | 1.4746 | 0
| 19:00 | 4.4 | Sat | WE | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 20:00 | 4.4 | Sat | WE | Off | Off | 22 | 20.24 | 1.76 | 1.7 | 3.3618 | 0.25 | 1035 | 1.5002 | 0
| 21:00 | 4.1 | Sat | WE | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 22:00 | 4.1 | Sat | WE | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0
| 23:00 | 4.1 | Sat | WE | Off | Off | 22 | 20.21 | 1.79 | 1.7 | 3.4191 | 0.25 | 1035 | 1.5257 | 0