## Rev 00
General Comments from Environmental Engineers
GLA carbon emissions calculator tool | At the time of producing the Energy Strategy (Summer 2022) the new SAP 10 software had not been fully developed. To that extent, the energy calculations for the residential element were completed using the current (at the time) SAP 2012 software. The energy calculations for the non-residential element was undertaken using the latest IES software under BR 2021. The GLA carbon emissions calculator tool could not be completed at that time as it was not possible to insert energy calculation results based on 2 different carbon conversion calcs. The Latest GLA Carbon emissions caluclator has been completed now, assuming gird electricity conversion factor of 0.136kgCO2/kWhr, which is different to both what was used for the residential and non-residential. With this in mind, the figures presented within the Energy Strategy report will be out of date.
Whole Life Carbon | WLC report was undertaken at the time but accidently mistaken from the full planning submission. Please find within the attached documents.
BREEAM | A 'base case' with a score of 71.76% has been identified. We have also identified a number of stretch target credits which could increase the score by circa. 6%, allowing for approx. 5% buffer in line with our reccomendations, clearly stated within the BREEAM report. We feel that we have presented sufficient information to indicate that BREEAM Excellent is achievable. As shell & core developments, we feel it is important to give the client some flexibility on where/how their focus their enviromental importance.
Action No. | Planners Response | Planners Action | WME response
1 | The proposals do not meet the requirement for zero carbon and therefore a carbon offset payment is required. This has been provisionally calculated as £24,026. | Figure to be confirmed on GLA Carbon emissions spreadsheet and secured through s106 | Refer to latest GLA carbon emissions tool attached
2 | There are no Notional Baseline calculations in Appendices 5 & 6 for SAP & BRUKL. All SAP & BRUKL results should additionally be presented in a summary table in order that we can verify the projected CO2 emission savings of 75.83%. | Further information required | Refer to folder with all energy calculation output sheets
3 | The GLA’s carbon emissions reporting spreadsheet is not included and there is no separate reporting of carbon reductions for residential uses, non-residential uses and the entire site as set out in 6.2 of the GLA Energy Assessment Guidance 2022 . | Further information required | Refer to latest GLA carbon emissions tool attached
4 | EUI information should be provided and shown to be within the benchmarks from table 4 of the GLA energy assessment guidance. | Further information required | Refer to latest GLA carbon emissions tool attached
5 | The Solar PV panel array does not maximise coverage over the available roof area, in accordance with Policy SI 2 of the London Plan major development should 'maximise opportunities for renewable energy'. It is further stated on Page 26 of the Energy Statement that, 'At the time of procurement of the PV panels for the roof, it will be appraised as to the best value obtainable and their Whole Life cost, in terms of type and efficiency. Compared against Carbon Offsetting, the PVs are currently not best value'. This approach goes against section 9.2.8 of the London Plan which states 'New development is expected to get as close as possible to zero-carbon on-site, rather than relying on offset fund payments to make up any shortfall in emissions'. Further justification that opportunities for renewable energy have been maximised & that the development has been designed to get as close as possible to zero-carbon on site should be submitted. |  | Refer to rooftop layout indicating proposed shield and implications on PV panels. IT is unlikely that there will be sufficient space for any additional PV panels. The required screen will cast a shadow on some of the already proposed PV panels and may affect their performance. Without going into detailed shading studies at the present time, we propose that those panels potentially affected by the shield are moved over to the western corner of the roof. In summary, we are happy to maximise the number of PV panels, however this may now be hindered by the requirement for a rooftop shield.
6 | Active cooling is proposed via the MVHR system. The applicant must fully demonstrate that the cooling hierarchy from the GLA Energy Assessment Guidance 2022 has been applied with a preference towards passive design measures and the use of active cooling as a last resort. 'Appendix 1 - Overheating risk assessment' only models the development with active cooling due to limitations on openable windows. Section 8.10 of GLA Energy Assessment Guidance 2022 outlines additional feasibility assessment and modelling the applicant should undertake in these circumstances. Alternative scenarios without active cooling should be modelled. It should be demonstrated if the development can achieve the thermal comfort criteria using measures further up the cooling hierarchy (Section 8.2 of GLA Energy Assessment Guidance 2022). There should be further modelling using CIBSE TM52 & TM49 datasets to separately model overheating in residential & non-residential areas of the building in line with guidance in Table 6 of GLA Energy Assessment Guidance 2022 |  | Our approach to reduce overheating in line with the cooling hierarchy: minimise internal heat gain through energy efficiency design - The footprint of the building is very much determined by the existing site - Dual aspect windows are not possible except for the end units between Finchley Road and College Cresecent - U values are better than the Notional building - No blinds have been assumed in the calculation. Minimise internal heat generation through energy efficient design - Natural surroundings have been included in the simulation. The building therefore benefit from solar shading. Manage the heat within the building through exposed internal thermal mass and high ceilings: - The percentage of glazed area on the facades has been carefully considered to help reduce solar gains into the rooms and reduce the amount of cooling required - Thermal mass will be exposed where possible and light coloured paints to be selected as part of the interior design scheme Provide Passive Ventilation: There is a generous provision of openable windows throughout each of the spaces, to this extent - natural ventilation is considered the primary means of mitigating overheating. Provide Mechanical Ventilation: The natural ventilation strategy is assisted by mechanical ventilation with heat recovery (MVHR) to both ventilate the WC’s, shower rooms, utility areas and kitchen areas, plus provide some useful reduction in energy consumption, recovering waste heat. On extreme hot weather days where it might not be desirable to have windows open, the MVHRs cooling module can provide mechanical cooling. A CIBSE TM59 Overheating Assessment was undertaken in coorperation with Build ENergy. Whilst a primiarly naturally ventilated strategy was the preferred option, it would only work with a significant number of additional fans added to make up 10 ach. Whilst a compliant solution was met in this manner, it was determined that the associated embodied carbon would significantly over rule it's selection. In relation to the Non-residential Units at lower ground and ground level - These are proposed as Shell & Core units at the present time. Whilst a commercial and educational space is preference at present, this is not confirmed. To this extent, it is felt that undertaking detailed overheating analysis at the present time and of a hypothetical space, is considered ineffective and economically unjustifiable within early planning budget constraints. We have used our experience and engineering judgement to determine that the limitations imposed by the footprint , combined with the very nature of a typical ground floor, street level commercial/educational space (consideration given to acoustics and air quality), in central london with ever increasing peak summer time temperatures, means that a mechanical ventilation strategy with active cooling will likely be required. Our Shell & Core design has endeavoured to follow the initial steps of the cooling hierarchy by allowing for insulation levels above that of the notional building.
7 | The minimum requirements for BREEAM have not been met. Additional credits for water should be targeted. BREEAM Excellent and at least 60% in Energy, 60% in Water and 40% in materials should be secured through s106. | Secure through s106 | It is not possible for us to achieve 60% in the water section as the development is Shell & Core only. There are no sanitary fittings for us to assess, therefore in line with BREEAM guidance we have to adatp default Base figures which equate to achieving 1/5 credits only. A Water Meter and A Leak Detection system we are happy to commit to, but we can't provide solendoid values as the sanitary fit out will be the sole responsibility of the tenant.
8 | If demolition is justified (see Chapter 9 of CPG Energy Efficiency) then a whole life carbon assessment is required. | Further information required | Refer to Pre-demlotion Audit contained within the Circular Economy Report - P150051-RPT-8003 Circular Economy Statement WME Revision 00
9 | No information on the proposed demolition is provided in the Sustainability statement. As set out in CPG Energy Efficiency chapter 9 the development proposal should include a pre-demolition audit identifying all materials within the building and documenting how they will be managed. The preference should be for re-use on site, then re-use off site, remanufacture or recycling. (Providing time in the project plan for selective deconstruction techniques and materials storage to maximise reuse). New London Plan policy SI7 expects 95% of construction and demolition waste to be diverted from landfill (reuse, recycle, recovery), and 95% of excavation waste to be put to beneficial use. | Further information required | Refer to Pre-demlotion Audit contained within the Circular Economy Report - P150051-RPT-8003 Circular Economy Statement WME Revision 00

## Rev 01
Planners Response |  | Planners Action | WME response
Air Quality | 1 | Particularly given the poor air quality in the area, the applicant should: • justify the proposed size of the generators, which should be sized appropriately for life safety functions only unless clearly justified for other reasons • alternative technologies to diesel should be fully considered • testing should be minimised | The generator is only needed as back up for the sprinkler system only and is sized accordingly. Alternative technologies (eg battery) have been investigated but are not a viable technical solution in this case. Testing will be carried out to the minimum essential requirement.
| 2 | Atmospheric dispersion modelling to NO2 and PM concentrations with and without the proposed development is required to be carried out in line with the CPG Air Quality. It should be noted that modelling should not predict improvements to future years (future vehicle emissions or future background concentrations). The WHO air quality guidelines in place at the time of the London Plan 2021 should be considered. | Fresh air for all apartments is either taken from the roof, or via the rear of the building, as far away as possible from Finchley Road. Exhaust air is sent to the nearest façade. Openable windows are not to provide general ventilation and are only intended for purge ventilation and an additional means for controlling overheating. Ventilation to the school accommodation is also to be taken from roof level to minimise risk of poor air quality. There is little purpose in carrying out atmospheric dispersion modelling given that air inlets are already proposed to be on the rear or roof of the building, as far away from Finchley Road as possible, and cannot be any further removed. It is important to note that the AQA utilised data, inter alia, from the permanent AQ monitoiring site at Swiss Cottage, just 200m south of the Site. Significantly, it showed a general downward trend in pollution levels associated with the ULEZ and increasing numbers of electric vehicles - and it is most unlikely to show any different AQ results than would a detailed model.
| 3 | The air quality for the school is a particular concern as it is located on the lower ground floor and will need to rely on the ventilation. It needs to be proven that the site is suitable for educational use, that the air at location of the air inlets is not polluted and that further mitigation such as filtration is not required. Confirmation that no natural ventilation is proposed for the educational use area is also requested. | It should be emphasised that the proposed educational use is not a new school, but rather an extension to the existing neighbouring school. There will be no increase in number of students, rather an increase in school floor area, providing a better ventilated space than the existing building, not only in terms of fewer students /m2 (equals > ventilation), but also by reducing the reliance on the existing classroom and gymnasium spaces curretnly fronting FInchley Road . The proposed new education space will be designed in accordance with the latest BB101 guidance on ventilation, thermal comfort and indoor air quality for schools
| 4 | Given the location in an area of poor air quality site specific modelling is required to determine if natural ventilation is suitable on all facades and levels. | Natural ventilation is not being proposed for the school accommodation.
| 5 | All measures relevant to the High dust risk for demolition, earthworks, construction and track-out from Appendix 7 of the Mayor of London's SPG on The Control of Dust and Emissions During Construction and Demolition should be incorporated in the CMP. This should include at least 4 real time dust monitors. | These measures can be secured through planning condition in relation to a detailed CMP following appointment of a contractor. Any real time monitoring to be undertaken should be addressed accordingly by the appointed contractor.
Energy | 1 | The proposals do not meet the requirement for zero carbon and therefore a carbon offset payment is required. This has been provisionally calculated as £24,026. Issues 2 & 3 will need to be resolved before agreeing a carbon offset payment | We understand that the carbon emissions calculations are preliminary only at this planning stage. We envisage that all calculations will be re-visited and ulimtately the final carbon emissions and financial contributions will be determined from the as-built calculations - and secured by planning obligation. Final calculations will be representative of exactly what is installed. The Modutherm unit is the preferred ASHP at this stage, based on it (see accompanying product data sheet). The COP of the ASHP is dependent on the external ambient temperature. It is fully acknowledged that it might not operate with a COP 4 all of the time. In terms of planning stage modelling, for residential uses, default values have been selected for a community ASHP system. At the next stage, the kit will be selected from the NCM product database and the exact COP profile applied within the calculation. It is worth noting that the default values within SAP do NOT tend to over rig the calculations, but instead give more cautious results. For the SBEM calculation we will reduce the CoP to circa 3 at the next stage of design.
| 2 | There are no Notional Baseline calculations in Appendices 5 & 6 for SAP & BRUKL. All SAP & BRUKL results should additionally be presented in a summary table in order that we can verify the projected CO2 emission savings of 75.83%. SAP & BRUKL sheets are provided, what is the assumed SCOP of the Communal ASHP as used in Be Green calculations? A COP of 4.0 is stated on page 17 of the Energy Statement, if this is the assumed SCOP could this be further justified as heat pumps are unlikely to deliver this level of efficiency on an annual basis.
| 3 | The GLA’s carbon emissions reporting spreadsheet is not included and there is no separate reporting of carbon reductions for residential uses, non-residential uses and the entire site as set out in 6.2 of the GLA Energy Assessment Guidance 2022 . Further information required: The spreadsheet has been provided - Space heating demand in the School is very low 1.18kWh/m2/yr, what is the justification for such a low figure? | Calculation has been re-visited to include for ventilation heating. Total Space heating Figure = 15.79 (spreadsheet updated).
| 4 | EUI information should be provided and shown to be within the benchmarks from table 4 of the GLA energy assessment guidance. - The EUI for residential element is exceeded, 45.5kwh.m2/yr vs target of 35. What is the justification for this? | Calculation has been re-visited, figures quoted were incorrect following discrepancy between old and new carbon conversion factors. EUI (kWh/m2/year) for dwellings has been recalculated to be approx. 27 kWh/m2/yr. NOTE: all calculations are to be updated at the next stage of design.
| 5 | We welcome inclusion of a Solar PV array at the site, we would ideally see this integrated with the design of the blue/green roof with solar panels appropriately spaced over the blue/green roof. The Solar PV panel array does not maximise coverage over the available roof area, in accordance with Policy SI 2 of the London Plan major development should 'maximise opportunities for renewable energy'. It is further stated on Page 26 of the Energy Statement that, 'At the time of procurement of the PV panels for the roof, it will be appraised as to the best value obtainable and their Whole Life cost, in terms of type and efficiency. Compared against Carbon Offsetting, the PVs are currently not best value'. This approach goes against section 9.2.8 of the London Plan which states 'New development is expected to get as close as possible to zero-carbon on-site, rather than relying on offset fund payments to make up any shortfall in emissions'. Further justification that opportunities for renewable energy have been maximised & that the development has been designed to get as close as possible to zero-carbon on site should be submitted. ACTION: Further information required - I accept argument on shading, provide updated plans with PV panels moved to the western corner to maximise coverage & reduce shading. | See revised drawing (to follow)
Sustainability | 6 | Active cooling is proposed via the MVHR system. The applicant must fully demonstrate that the cooling hierarchy from the GLA Energy Assessment Guidance 2022 has been applied with a preference towards passive design measures and the use of active cooling as a last resort. 'Appendix 1 - Overheating risk assessment' only models the development with active cooling due to limitations on openable windows. Section 8.10 of GLA Energy Assessment Guidance 2022 outlines additional feasibility assessment and modelling the applicant should undertake in these circumstances. Alternative scenarios without active cooling should be modelled. It should be demonstrated if the development can achieve the thermal comfort criteria using measures further up the cooling hierarchy (Section 8.2 of GLA Energy Assessment Guidance 2022). There should be further modelling using CIBSE TM52 & TM49 datasets to separately model overheating in residential & non-residential areas of the building in line with guidance in Table 6 of GLA Energy Assessment Guidance 2022 Further consideration of passive measures is required, it should not be necessary to have active cooling in well-designed new residential space (GLA Energy Assessment Guidance 2020 section 8.20). Key to this is having an effective ventilation strategy i.e. twin-aspect cross-ventilation & night-time purge ventilation, & effective passive measures i.e. solar shading with bris-soleil, consideration of fenestration and g-values i.e. solar control glass. The cooling hierarchy should be fully considered with relevant measures further up the cooling hierarchy modelled, overheating must be demonstrated without active cooling. Dynamic thermal modelling should be undertaken as outlined in section 8 of GLA Energy Assessment Guidance. Comment: Many of the apartments are single aspect preventing opportunity for cross-ventilation which may exacerbate overheating. Overheating could further be exacerbated as apartments facing the Finchley Road will likely have limitations on openable windows due to noise and air quality concerns. | Our approach to reduce overheating in line with the cooling hierarchy: Minimise internal heat gain through energy efficiency design - The footprint of the building is very much determined by the existing site configuration - Dual aspect windows are not possible except for the end units between Finchley Road and College Cresecent - U values are better than the Notional building - No blinds have been assumed in the calculation. Minimise internal heat generation through energy efficient design - Natural surroundings have been included in the simulation. The building therefore benefit from solar shading. Manage the heat within the building through exposed internal thermal mass and high ceilings: - The percentage of glazed area on the facades has been carefully considered to help reduce solar gains into the rooms and reduce the amount of cooling required - Thermal mass will be exposed where possible and light coloured paints to be selected as part of the interior design scheme Provide Passive Ventilation: There is a generous provision of openable windows throughout each of the spaces, to this extent - natural ventilation is considered the primary means of mitigating overheating. Provide Mechanical Ventilation: The natural ventilation strategy is assisted by mechanical ventilation with heat recovery (MVHR) to both ventilate the WC’s, shower rooms, utility areas and kitchen areas, plus provide some useful reduction in energy consumption, recovering waste heat. On extreme hot weather days where it might not be desirable to have windows open, the MVHRs cooling module can provide mechanical cooling.
A CIBSE TM59 Overheating Assessment was undertaken in coorperation with Build ENergy. Whilst a primiarly naturally ventilated strategy was the preferred option, it would only work with a significant number of additional fans added to make up 10 ach. Whilst a compliant solution was met in this manner, it was determined that the associated whole life carbon would rule out its selection. In relation to the non-residential Units at lower ground and ground level - these are proposed as shell & core units at this stage . Whilst a commercial and educational space is preferred, this is not confirmed. In this context, undertaking detailed overheating analysis is considered ineffective and economically unjustifiable within early planning budget constraints. Rather, we have used our experience and engineering judgment to determine that the limitations imposed by the footprint , combined with the nature of a typical ground floor, street level commercial/educational space (consideration given to acoustics and air quality), in central london with ever increasing peak summertime temperatures, means that a mechanical ventilation strategy with active cooling will likely be required. Our shell & core design has endeavoured to follow the initial steps of the cooling hierarchy by allowing for insulation levels above that of the notional building. Additional Comments - brise soleil and shading is not possible as they would impact on the daylighting standards within the occupied spaces. It should be noted that the proposed strategy is intended to be used only in extreme temperature situations. The cooling module will enable a solution where the air change rates within the dwelling can be boosted up to 4 air changes per hour. This is intended to reduce the reliance on the natural ventilation required to provide overheating mitigation, reducing the number of hours the windows will be open where ambient noise levels can be better managed.
BREEAM | 7 | BREEAM The BREEAM overall base case score is 71.16% which would meet the requirement for BREEAM Excellent. • Energy targeted credits 12 out of 19 = 63% which meets the requirement of 60% • Water targeted credits 3 out of 8 = 38% which does not meet the requirement of 60% • Materials targeted credits 9 out of 14 = 64% which meets the requirement of 40% Comment: BREEAM Excellent is narrowly met, we would wish to see this requirement exceeded by a larger margin to ensure the as-built development will achieve BREEAM Excellent. Issue 7: The minimum requirements for BREEAM have not been met. Additional credits for water should be targeted. BREEAM Excellent and at least 60% in Energy, 60% in Water and 40% in materials should be secured through s106. ACTION: Applicant states water target cannot be achieved as assessment is for shell and core only. The 60% of water credits should be secured through s106 in the final fit out. | Noted/agreed