|  | ENVIRONMENTAL HEALTH SUPPORTING COMMUNITIES |
| --- | --- |

| To: | Adam Greenhalgh, Planning Officer, Development Management, 5 Pancras Square |
| --- | --- |
| From: | Edward Davis (Environmental Health Officer) |
| Date: | 01 March 2023 |
| Re: | 25 Rathbone Place London Camden W1T 1JB |
| Proposal: | Erection of rear extension at second floor level, addition of roof terrace on third floor roof, Juliet balconies at rear on first, second and third floor levels and alterations to rear fenestration all in connection with the change of use of first to third floors from ancillary public house accommodation (Sui Generis) to residential flats (Class C3) comprising one x 1-bed and two x 2-bed. Excavation at basement level to increase floor to ceiling heights and a new extract duct to rear elevation associated with the existing public house. |
| Reference: | Planning application ref. 2022/4321/P |
| Key Points: | The proposals are acceptable in environmental health terms |

# ENVIRONEMTAL HEALTH OBERVATIONS

An acoustic assessment has been submitted in support for the change of use of first to third floors from ancillary public house accommodation to residential flats a new extract duct to rear elevation associated with the existing public house.

Appropriate noise guidelines have been followed within the report such as Noise Policy Statement for England, National Planning Policy Framework (NPPF), Planning Practice Guidance on Noise, BS 8233 Guidance on sound insulation and noise reduction for buildings, Camden Council’s Local Plan, version June 2017 and o BS 4142:2014 “Methods for rating and assessing industrial and commercial sound”.

Fascade noise levels have been adequately measured and assessed pursuant to BS8233:2014 and the plant noise criteria have been adequately predicted  taking into consideration distance losses, surface acoustic reflections and, where applicable, screening provided by the building.

The assessment indicates that the proposed plant should be capable of achieving the proposed environmental noise criteria at the nearest and potentially most affected noise sensitive receptors and that adequate façade design can be constructed to protect future occupiers.

I am satisfied that the submitted acoustic submission meets our local plan guidelines and therefore acceptable in environmental health terms.  I offer no objections to the application and suggest the following should you be mindful to grant the application.

Suggested conditions:

The external noise level emitted from plant, machinery or equipment at the development with specified noise mitigation hereby approved shall be lower than the typical existing background noise level by at least 10dBA, by 15dBA where the source is tonal, as assessed according to BS4142:2014 at the nearest and/or most affected noise sensitive premises, with all machinery operating together at maximum capacity and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by noise from mechanical installations/ equipment in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

Prior to use, machinery, plant or equipment at the development shall be mounted with proprietary anti-vibration isolators and fan motors shall be vibration isolated from the casing and adequately silenced and maintained as such.

Reason: To ensure that the amenity of occupiers of the development site and surrounding premises is not adversely affected by vibration in accordance with the requirements of policies A1 and A4 of the London Borough of Camden Local Plan 2017

The design and structure of the development shall be of such a standard that it will protect residents within it from existing external noise so that they are not exposed to levels indoors of more than 35 dB LAeq 16 hrs daytime and of more than 30 dB LAeq 8 hrs in bedrooms at night.

The installation, operation, and maintenance of the odour abatement equipment and extract system, including the height of the extract duct and vertical discharge outlet must be in accordance with the ‘EMAQ+Control of Odour and Noise from

Commercial Kitchen Exhaust Systems.  Approved details shall be implemented prior to the commencement of the use and thereafter be permanently retained.

Reason: To ensure that the amenity of occupiers of the development site/ surrounding premises is not adversely affected by cooking odour

Regards

Edward Davis

Pollution Planning Officer

Supporting Communities

London Borough of Camden

Telephone:   02079745550/ Mobile: 07967 652382